## Sheet1
Water Use Efficiency Compliance Documentation – Directions
Compliance Forms
Compliance forms are provided in the User’s Manual to assist in understanding and documenting compliance with each section's requirements.
To demonstrate compliance with the Standard’s requirements for this section, projects must demonstrate compliance with mandatory measures.
Header Information
Project Name: Enter the name of the project. This should agree with the name that is used on the plans and specifications or the common name used to refer to the project.
Project Address: Enter the street address of the project, for instance “949 Main Street, Irvine, CA 92618.”
Date: Enter the date when the compliance documentation was completed.
Designer of Record/Telephone: Enter the name and the telephone number of the designer of record.
Contact Person/Telephone: Enter the name and telephone number of the person who should be contacted if there are questions about the compliance documentation.
City: The city where the project is located.
Instructions
For each item in the compliance forms, there is the option to indicate that 1) the project complies with the requirement or 2) the requirement is not applicable to the project. Select the appropriate check box.
If a requirement's exception(s) apply to the project, check the appropriate box.
For every item checked "complies," the documentation author should fill in the Document Reference field by citing the plans (drawing number), specifications (specifications section number), or attached calculations that document the requirement.
The documentation author should fill in the Calculated Performance Metric field on the Performance Option form with the results of applicable performance metric calculations.

## Sheet2
Water Use Efficiency Compliance Documentation – Mandatory
Project Name
Project Address: |  |  | Date:
Designer of Record: |  |  | Telephone:
Contact Person: |  |  | Telephone:
City:
Mandatory Provisions
Complies | Not applicable | Requirement | Document Reference
§601.3.1: Site Water Use Reductions
q | q | §601.3.1.1: Minimum of 60% of the area of the improved landscape shall be in bio-diverse planting of native plants and rainfall-ETc compatible plants.
qExceptions: 1.The area of dedicated athletic fields, golf courses, driving ranges, and areas dedicated for production of food for human consumption shall be excluded from the calculation of the improved landscape for schools, residential common areas, or public recreational facilities.  2.Landscape areas irrigated solely with alternate on-site sources of water shall be exempt from these requirements.  3.Where average annual rainfall is less than 12 in. (300 mm), plants other than turfgrass, with an annual ETc of 15 in. (380 mm) or less, shall be deemed equivalent to rainfall-ETc compatible plants.
q | q | §601.3.1.2: Irrigation. For landscaped areas, not greater than one-third of improved landscape area is allowed to be irrigated with potable water. The area of dedicated athletic fields shall be excluded from the calculation of the improved landscape for schools, residential common areas, and public recreational facilities. All other irrigation shall be provided from alternate sources of water.
q Exception: The amount of potable water used during the landscape establishment period does not exceed 70% ETo for turfgrass and 55% ETo for other plantings.
q | q | §601.3.1.2.1: The irrigation system is designed by an accredited or certified irrigation professional and following the requirements of the following.  a.Irrigation systems: 1.Shall be based on hydrozones. Turfgrass areas shall be on their own irrigation stations. 2.Shall have backflow prevention in accordance with the plumbing code (Informative note: e.g., International Plumbing Code). 3.[JO] Shall have a master valve on municipally supplied water sources that allows pressurization of the irrigation mainline only when irrigation is scheduled. 4.[JO] Shall have a flow sensor and monitoring equipment that will shut off the control valve if the flow exceeds normal flow from an irrigation station. 5.Shall prevent piping from draining between irrigation events.  b.Irrigation emission devices shall comply with ASABE/ICC 802, Landscape Irrigation Sprinkler and Emitter Standard.  c.Irrigation sprinklers: 1.Shall not spray water directly on buildings or hardscape area. 2.Shall have matched precipitation rate nozzles within an irrigation station. 3.Shall be prohibited on landscape areas having any dimension less than 4 ft (1.2 m). 4.Shall have an application rate less than or equal to 0.75 in. (19 mm) per hour on slopes greater than 1 unit vertical in 4 units horizontal. 5.Shall be limited to use with turfgrass or ground cover areas with vegetation maintained at 8 in. (200 mm) or less in height. 6.Where of the pop-up configuration, shall have a pop-up height of not less than 4 in. (100 mm).  d.Microirrigation zones: 1.Shall be equipped with pressure regulators, filters, and flush assemblies. 2.Shall have indicators that allow confirmation of operation by visual inspection. 3.Drip emitters shall be of pressure-compensating type.
q | q | §601.3.1.2.1: Sprinklers are not spraying water directly on a building and are not located within 3 ft (0.92 m) of any building.
q | q | §601.3.1.2.2: Controls. Where any irrigation system for the project site uses an automatic controller, the system shall be controlled by a qualifying smart controller that uses evapotranspiration (ET) and weather data to adjust irrigation schedules and complies with the minimum requirements. Alternatively, the system shall be controlled by an on-site rain or moisture sensor that automatically shuts off the system after a predetermined amount of rainfall or sensed moisture in the soil. Qualifying smart controllers shall be labeled according to USEPA WaterSense Specification for Weather-Based Irrigation Controllers or tested in accordance with Irrigation Association SWAT Climatologically Based Controllers, 8th Testing Protocol. Smart controllers that use ET data shall provide the following irrigation amounts: a.Irrigation adequacy—80% minimum ETc. b.Irrigation excess—not to exceed 10% of ETc. Exception: A temporary irrigation system used exclusively for the establishment of new landscape shall be exempt from this requirement. Temporary irrigation systems shall be removed or permanently disabled at such time as the landscape establishment period has expired.
q | q | §601.3.1.2.2: Smart controller uses evapotranspiration and weather data or on-site rain sensors or moisture sensors to adjust irrigation schedules.
q | q | §601.3.1.2.2: Qualifying smart controllers meet the following minimum requirements: irrigation adequacy – 80 % min ETo; irrigation excess – not to exceed 10%.
q Exception: Temporary irrigation systems used for plant establishment are exempt from this requirement.
q | q | 601.3.1.2.2.1 (6.3.1.2.2.1). The following settings and schedule for the irrigation control system shall be posted on or adjacent to the controller: a.Precipitation rate of each irrigation station. b.Plant factors for each hydrozone. c.Soil type. d.Rain sensor settings. e.Soil moisture sensor settings, where installed. f.Peak demand schedule, including run times, cycle starts, and soak times. g.Maximum runtimes to prevent water runoff.
q | q | §601.3.1.2.3: The use of potable water or reclaimed water for irrigation of adapted plants is prohibited after the landscape establishment period. In-ground irrigation systems for rainfall-ETc compatible plants using potable water or off-site treated reclaimed water are prohibited. Exception:Plants deemed equivalent to rainfall-ETc compatible plants by Section 601.3.1.1 (6.3.1.1), Exception 3, shall be exempt from the requirements of Section 601.3.1.2.3 (6.3.1.2.3).
§601.3.2: Building Water Use Reductions
q | q | §601.3.2.1a: Water closets (flushometer) have a max flush rate of 1.28 gal (4.8 L) per flush.
q | q | §601.3.2.1b: Water closets (tank-type) have a max flush rate of 1.28 gal (4.8 L) per flush.
q | q | §601.3.2.1c: Urinals have a max flush rate of 0.5 gal (1.9 L) per flush.
q | q | §601.3.2.1d: Public lavatory faucets have a max flow rate of 0.5 gpm (1.9 L/min).
q | q | §601.3.2.1e: Public metering faucets have a max flow rate of 0.25 gal (1.0 L) per cycle.
q | q | §601.3.2.1f: Residential lavatory faucets have a max flow rate of 1.5 gpm (5.7 L/min).
q | q | §601.3.2.1g: Residential kitchen faucets have a max flow rate of 2.2 gpm (8.3 L/min).
q | q | §601.3.2.1h: Residential showerheads have a max flow rate of 2.0 gpm (7.6 L/min).
q | q | §601.3.2.1i: Residential shower compartments have a total max flow rate of 2.0 gpm (7.6 L/min).
q Exception: If the shower compartment exceeds 2,600 in2 (1.7 m2), an additional flow of 2.0 gpm (7.6 L/min) is permitted.
q | q | §601.3.2.1j: Water-bottle filling stations are included in at least half of all drinking fountains installed indoors.
q | q | §601.3.2.2a(1.): Dwelling unit clothes washers comply with the ENERGY STAR Program Requirements and have a max water factor of 5.4 gal/ft3 or 0.72 L/L of drum capacity.
q | q | §601.3.2.2a(2): Dwelling unit dishwashers comply with the ENERGY STAR Program Requirements and have a max water factor of 3.8 gal or 14.3 L/full operating cycle.
q | q | §601.3.2.2b: Publicly accessible clothes washer have a max water factor of 4.0 gal/ft3 or 0.53 L/L of drum capacity.
q | q | §601.3.2.2c: Commercial dishwashers in commercial food service facilities meet all ENERGY STAR requirements. V2.0
q | q | §601.3.2.3a: Potable water has not been used for once-through cooling in HVAC systems.
q | q | §601.3.2.3b: The design of open-circuit cooling towers for air-conditioning systems shall not allow water exchange (blowdown) until one or more of the parameters in Table 601.3.2.3 (6.3.2.3) reaches 90% or more of the maximum value specified in Table 601.3.2.3 (6.3.2.3). The system shall be tolerant of pH levels between 7.0 and 9.2.
q | q | §601.3.2.3c: The materials of construction for the water cooling system that comes in contact with cooling tower water shall be of the type that can operate and be maintained within the limits set in Table 601.3.2.3 (6.3.2.3).
q | q | §601.3.2.3d: Open-circuit cooling towers, closed-circuit cooling towers, and evaporative condensers shall be equipped with makeup and water meters, conductivity controllers, and overflow alarms in accordance with the thresholds listed in Table 601.3.4.1B (6.3.4.1B). Cooling towers shall be equipped with drift eliminators that reduce drift to 0.002% or less of the recirculated water flow for counterflow towers and 0.005% or less of the recirculated water flow for cross-flow towers.
q | q | §601.3.2.3e: Building projects located in regions where the ambient mean coincident wet-bulb temperature at 1% design cooling conditions is greater than or equal to 72°F (22°C) shall have a system for collecting condensate from air-conditioning units with a capacity greater than 65,000 Btu/h (19 kW), and the condensate shall be recovered for reuse.
601.3.2.4 a. Roof spray systems did not use potable water or reclaimed water. Exception: Where approved, on-site treated reclaimed water may be used for roof spray systems. b.In-ground irrigation systems on vegetated roofs using potable water or off-site treated reclaimed water shall be prohibited. c.The use of potable water or reclaimed water for irrigation of vegetated (green) roofs is prohibited after the vegetation establishment period or 18 month after the initial installation, whichever is less. After the landscape plants are established, the irrigation system using potable water or reclaimed water shall be removed from site. Exception: Where approved, on-site treated reclaimed water may be used for vegetated roof irrigation systems during and after the vegetation establishment period.
q | q | §601.3.2.5a: Commercial food service operations use high-efficiency pre-spray valves per §601.3.2.5.
q | q | §601.3.2.5b: Commercial food service operations use dishwashers that are ENERGY STAR certified.
q | q | §6.3.2.5c: Commercial food service operations use boilerless/connectionless food steamers that consume no more than 2.0 gal/h (7.5 L/h).
q | q | §6.3.2.5d: Commercial food service operations use combination ovens that consume no more than 10 gal/h (38 L/h).
q | q | §6.3.2.5e: Commercial food service operations use air-cooled ice machines that are ENERGY STAR certified.
q | q | §601.3.2.5f: Commercial food service operations are equipped with hands-free faucet controllers within the food preparation area of the kitchen and dish room, including pot sinks and washing sinks.
q | q | §601.3.2.6: a. Medical and lab facilities use only water-efficient steam sterilizers.
q | q | §601.3.2.6: b. Use film processor water-recycling units where large-frame X-ray films of more than 6 in. (150 mm) in either length or width are processed.
q | q | §6.3.2.6: c. Use digital imaging and radiography systems where the digital networks are installed.
q | q | §6.3.2.6: d. Use a dry-hood scrubber system or, if the applicant determines that a wet-hood scrubber system is required, the scrubber shall be equipped with a water recirculation system.
q | q | §6.3.2.6: e. Use only dry vacuum pumps
q | q | §6.3.2.6: f. Use only efficient water treatment systems
q | q | §6.3.2.6: f(1) For filtration processes in medical and lab facilities, pressure gauges are used to determine and display when to backwash or change cartridges.
q | q | §6.3.2.6: f(2) For ion exchange and softening processes in medical and lab facilities, recharge cycles have been set by volume of water treated or based upon conductivity or hardness.
q | q | §6.3.2.6: f(3) For reverse osmosis and nanofiltration equipment in medical and lab facilities with a capacity > 100 L/hour, reject water does not exceed 60% of the feed water and is used as scrubber feed water or for other beneficial uses on the project site.
q | q | §6.3.2.6: f(4) For medical and lab facilities, simple distillation has not been used as a means of water purification.
q | q | §601.3.2.6g: Food service operations that are located within medical or lab facilities comply with §601.3.2.5.
§601.4: Hot-water distribution
q | q | 601.3.3.1 The volume of water in the pipes between the source of hot or tempered water and the fixtures is a maximum of 64 oz (1.9 L) where the source of hot or tempered water is a water heater, and shall be 24 oz (0.71 L). The volume calculated is the sum of the internal volumes of pipe, fittings, valves, meters, and manifolds between the source of hot or tempered water and the termination of the fixture supply pipe. The volume shall be determined using Table 601.3.3.1. Exception: Public lavatory fixtures.
q | q | 601.3.3.2 The pipe length from the source of hot or tempered water to the termination of the fixture supply pipe serving any plumbing fixture or appliance does not exceed 50 ft (15 m) of developed length.
§601.3.4: [JO] Special Water Features
q | q | §601.3.4: a. Ornamental fountains are supplied either by alternate on-site sources of water or municipally reclaimed water.
q | q | §601.3.4: a. Fountains are equipped with makeup water meters.
q | q | §601.3.4: a. Fountains are equipped with leak detection devices that shut off water flow if a leak of more than 1 gallon per hour is detected.
q | q | §601.3.4: a. Fountains are able to recirculate, filter, and treat all water for reuse within the system.
q Exception: For fountains where alternate on-site sources of water or municipally reclaimed water are not available with 500 ft (150 m) of the building project site, potable water is allowed to be used for water features with less than 10,000 gal (38,000 L) capacity.
q | q | §601.3.4: b(1) Pools and spas must recover filter backwash water for reuse on landscaping or other applications, or treat and reuse backwash water within the system.
q | q | §601.3.4: b(2) For pools and spas that use removable cartridges, only reusable cartridges and systems are used.
q | q | §601.3.4: b(2) For pools and spas that contain filters with backwash capabilities, only pool filter equipment has been used that includes a pressure drop gauge to determine when the filter needs to be backwashed and a sight glass enabling the operator to determine when to stop the backwash cycle.
q | q | §601.3.4: b(3) If pool and spa splash troughs are provided, they drain back into the pool or spa.
§601.3.4: Water Consumption Measurement
q | q | §601.3.5.1: Measurement devices with remote communication capability have been provided to collect the water consumption data for each water supply source (e.g., potable, reclaimed, rainwater) to the building that exceeds the thresholds listed in Table 6.3.3A.
q | q | §601.3.5.1: Both potable and reclaimed water entering the building are being monitored or sub-metered.
q | q | §601.3..1: Sub-meters have been provided for individual leased, rented, or other tenant or sub-tenant space with any building totaling > 50,000 ft2 (5000 m2).
q | q | §601.3.5.1: Sub-meters have been provided for any project, building, tenant, or sub-tenant space within a project or building where water consumption > 1,000 gal/day (3800 L/day) or per Table 6.3.4.1.A.
q | q | §601.3.5.1: Sub-metering with remote communication capabilities has been provided to collect water use data for each of the subsystems listed in Table 6.3.4.1.B.
q | q | §601.3.5.2: [JO] Measurement devices installed on systems using more than 1,000 gal/day (3800 L/day) of water are configured to communicate water consumption data to a meter data management system. At a minimum meters provide daily data and record hourly consumption of water.
q | q | §601.3.5.3: [JO] The meter data management system is capable of electronically storing water meter, monitoring systems, and sub-meter data.
q | q | §601.3.5.3: [JO] The meter data management system creates user reports showing calculated hourly, daily, monthly, and annual water consumption for each measurement device and sub-meter.
q | q | §601.3.5.3: [JO] The meter data management system provides alarm notification capabilities to support the requirements of §1001.9.2.
§601.3.6: Water Softeners
q | q | §601.3.6.1: Water softeners are equipped with demand-initiated regeneration control systems (no timer-base systems).
q | q | §601.3.6.2: Water softeners shall have a maximum water consumption during regeneration of more more than 4 gal per 1000 grains of hardness removed (15.1 L per 17.1 g/L).
q | q | §601.3.6.3: Waste water from water softener regeneration does not discharge to reclaimed water collection systems and follows the IPC.
q | q | §601.3.6.4: Water softeners that regenerate in place, that are connected to the water system they serve by piping not exceeding 11/4 in. (31.8 mm) in diameter, or that have a volume of 3 ft3(0.085 m3)
§601.3.7: Reverse Osmosis Water Treatment Systems
q | q | §601.3.7.1: Reverse osmosis systems are equipped with an automatic shutoff valve.
q | q | §601.3.7.1: Point-of-use reverse osmosis treatment system for drinking water are listed and labeled to NSF 58.
§601.3.8: On-Site Reclaimed Water Treatment
q | q | §601.3.8: On-site reclaimed water treatment systems are listed and labeled in accordance with NSF 350.
§601.3.9: Dual Water Plumbing Supply
q | q | §601.3.9.1: The building water supply system has been constructed to allow the supply of reclaimed or alternative water to all urinals and water closets.
q Exception: the building scope of work does not include water supply systems for urinals or water closets, or the toilets or urinals are designed to operate without the use of water.
q Exception: sufficient supply of reclaimed water or alternate on-site sources of water are not available or expected to be available per section 6.3.8.1.
Signature: Date:
Printed Name: License/Registration #:
Company Name: