## IECC-credit-tables-PC
2022-10-21
Final resultant Energy Efficiency Credits in 2024 IECC, kBtu based, as currently published adjusted with suggested PNNL Public Comment changes
| CEDI- | PNNL Public Comment changes affecting credits are as follows:
| 185 | Editorial changes to match as voted; correct CZ 6B requirements; R-1/2: E01-06, round up 0 to 1 credit
| 172 | W09 SHW flow reduction measure and credits revised for R-1, R-2
| 190 | Allows carryover of excess renewable/load management credits to energy efficiency credits
| 192 | Reduce renewable/load management requirement based on 0.4 w/sf to -0.2 w/sf renewable
| 194 | Update E02 15% UA reduction credits based on improved analysis
Measures used in May 2022 Cost-effective Demonstration Package
| ID | Energy Credit Measure | Measure Life, yr | Multifamily | Healthcare | Hotel/Motel | Office | Restaurant | Retail | Education | Warehouse
| E01 | Glazing U & SHGC reduction | 40 | CZ 0A-1A | all CZ | all CZ | all CZ |  |  | all CZ
| E02 | Envelope 15% UA reduction | 40 | [5 empty] | CZ 4-8
| H02 | Heating efficiency | 18 |  | 5%, CZ 5-8 |  |  |  | 5%, CZ 7-8 |  | 10%, CZ 4-8
| H03 | Cooling efficiency. | 15 | 10% CZ 0-2 | 15%, CZ 0-2 | 15%, CZ 0-2 | 15%, CZ 0-2 | 15%, CZ 0-2 | 15%, CZ 0-3B | CZ 0-3B | CZ 0-3B
| H04 | Residential HVAC control. | 15 | all CZ
| W02 | Heat pump water heater or HR | 19 |  | 30% all CZ | 30% all CZ |  | 30% all CZ | CZ 0-5 |  | CZ 3
| W03 | Efficient gas water heater | 15 | 50% all CZ | 70% all CZ | 70% all CZ |  | 70% all CZ
| W05 | Point of use water heater | 15 |  |  |  | all CZ |  |  | all CZ
| W06 | Thermostatic balancing valves | 15 |  | all CZ | all CZ
| W08 | SWH flow reduction | 15 | all CZ |  | all CZ
| L04 | Increase daylighting area | 15 | [5 empty] | 10% CZ 0-6 |  | 5% all CZ
| L06 | Light power reduction | 20 | 5% all CZ | 10% all CZ | 10% all CZ | 10% all CZ | 10% all CZ | 10% all CZ | 10% all CZ | 10% all CZ
| Q02 | Efficient kitchen equipment | 15 |  |  |  |  | all CZ
| Q04 | Fault detection | 15 |  | all CZ | all CZ | all CZ |  | CZ 4B, 7-8 | all CZ
Final resultant Energy Credits in IECC, kBtu based, as currently published adjusted with suggested PNNL Public Comment changes
2022-10-21
Current requirements (with PNNL PC changes) for IECC 2024 (may be subject to change due to other proposals or modifications)
TABLE C406.1.1
ENERGY CREDIT REQUIREMENTS BY BUILDING OCCUPANCY GROUP
|  | Building Occupancy Group |  | Climate Zone
|  |  |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
|  | R-2, R-4, and I-1 | Apartment | 65 | 66 | 67 | 77 | 80 | 86 | 80 | 81 | 90 | 86 | 90 | 90 | 86 | 90 | 90 | 70 | 89 | 80 | 78
|  | I-2 | Health | 43 | 42 | 38 | 37 | 36 | 38 | 32 | 32 | 30 | 36 | 36 | 35 | 43 | 43 | 44 | 46 | 47 | 50 | 53
|  | R-1 | Hotel | 63 | 62 | 66 | 65 | 70 | 71 | 77 | 80 | 84 | 81 | 83 | 88 | 85 | 86 | 90 | 83 | 87 | 87 | 85
|  | B | Office | 62 | 62 | 64 | 66 | 66 | 65 | 64 | 64 | 68 | 70 | 72 | 74 | 71 | 73 | 77 | 71 | 74 | 74 | 71
|  | A-2 | Restaurant | 70 | 70 | 72 | 72 | 75 | 75 | 70 | 73 | 82 | 69 | 74 | 78 | 67 | 72 | 78 | 60 | 67 | 57 | 51
|  | M | Retail | 80 | 79 | 83 | 79 | 81 | 84 | 67 | 74 | 87 | 80 | 66 | 65 | 79 | 62 | 50 | 75 | 67 | 75 | 58
|  | E | Education | 56 | 57 | 55 | 58 | 58 | 57 | 59 | 62 | 59 | 61 | 66 | 62 | 64 | 67 | 67 | 65 | 67 | 63 | 58
|  | S-1 and S-2 | Warehouse | 61 | 60 | 61 | 60 | 58 | 57 | 44 | 54 | 62 | 85 | 68 | 75 | 90 | 82 | 72 | 90 | 89 | 90 | 90
|  | All Other | Other | 31 | 31 | 31 | 32 | 32 | 33 | 30 | 32 | 36 | 35 | 35 | 35 | 37 | 36 | 36 | 36 | 37 | 36 | 34
|  | TABLE C406.1.2 |  |  | Updated by PEDI-192
RENEWABLE AND LOAD MANAGEMENT CREDIT REQUIREMENTS BY BUILDING OCCUPANCY GROUP
|  | Building Occupancy Group |  | Climate Zone
|  |  |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
|  | R-2, R-4, and I-1 | Apartment | 34 | 37 | 31 | 46 | 48 | 56 | 49 | 56 | 38 | 31 | 42 | 32 | 26 | 33 | 34 | 23 | 27 | 25 | 25
|  | I-2 | Health | 23 | 24 | 25 | 25 | 25 | 28 | 26 | 30 | 22 | 25 | 32 | 24 | 25 | 28 | 29 | 26 | 28 | 22 | 20
|  | R-1 | Hotel | 30 | 28 | 35 | 30 | 34 | 36 | 34 | 37 | 41 | 32 | 37 | 27 | 28 | 33 | 32 | 25 | 29 | 22 | 18
|  | B | Office | 38 | 39 | 45 | 42 | 45 | 49 | 47 | 56 | 57 | 44 | 55 | 42 | 38 | 47 | 46 | 38 | 45 | 38 | 31
|  | A-2 | Restaurant | 8 | 8 | 9 | 9 | 8 | 9 | 9 | 11 | 13 | 8 | 11 | 9 | 8 | 10 | 9 | 8 | 9 | 8 | 3
|  | M | Retail | 32 | 32 | 42 | 37 | 39 | 43 | 43 | 55 | 51 | 40 | 47 | 39 | 38 | 43 | 42 | 36 | 42 | 36 | 28
|  | E | Education | 27 | 34 | 38 | 37 | 39 | 47 | 44 | 58 | 57 | 42 | 54 | 46 | 38 | 48 | 50 | 42 | 45 | 38 | 34
|  | S-1 and S-2 | Warehouse | 89 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 84 | 86 | 71 | 54
|  | All Other | Other | 35 | 39 | 46 | 42 | 46 | 52 | 49 | 56 | 56 | 40 | 52 | 42 | 37 | 44 | 44 | 36 | 39 | 32 | 28
|  | Combined Available Energy & Renewable/Load Management Credits | [10 empty] | BY BUILDING OCCUPANCY GROUP
|  | Building Occupancy Group |  | Climate Zone
|  |  |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
|  | R-2, R-4, and I-1 | Apartment | 359.8 | 365.4 | 351.6 | 418.6 | 419.8 | 473 | 463.8 | 468.2 | 485.6 | 423.4 | 463.8 | 447.6 | 497.4 | 459.4 | 462.6 | 472.8 | 475.6 | 471.2 | 456
|  | I-2 | Health | 131.2 | 132.2 | 128.2 | 127.2 | 131.2 | 159.8 | 143.8 | 146.8 | 155.8 | 140.8 | 154.8 | 150.8 | 171.8 | 153.8 | 164.8 | 149.8 | 154.8 | 155.8 | 148.8
|  | R-1 | Hotel | 188.6 | 181.2 | 207.4 | 186.4 | 197.6 | 217.2 | 209.4 | 218.4 | 249 | 227.6 | 221.6 | 207.4 | 228.8 | 219.8 | 222 | 232.2 | 227.8 | 232.8 | 216.2
|  | B | Office | 183 | 194 | 206.6 | 201.6 | 206.2 | 208.2 | 211.8 | 231.2 | 239.8 | 218.8 | 230.8 | 207.4 | 214.8 | 222.8 | 223.4 | 214.8 | 234.8 | 238.4 | 213.8
|  | A-2 | Restaurant | 155 | 149.6 | 164.4 | 154.8 | 176.6 | 162.2 | 185.8 | 169.4 | 183.8 | 200.4 | 176 | 182.2 | 217.8 | 192 | 180.2 | 225.6 | 208.4 | 225.6 | 194.8
|  | M | Retail | 203.6 | 220.2 | 246.8 | 231.8 | 242 | 248 | 288 | 293.6 | 283.4 | 329.4 | 276.6 | 287.6 | 343.8 | 305 | 304.6 | 348.2 | 335.8 | 329.8 | 265.2
|  | E | Education | 185.4 | 215.4 | 227.6 | 224 | 230.6 | 256.2 | 257.8 | 286.8 | 282.4 | 251.4 | 287.4 | 274 | 254.4 | 296.4 | 270.6 | 271.8 | 283 | 275.4 | 269.2
|  | S-1 and S-2 | Warehouse | 374.4 | 408.4 | 495 | 445.4 | 474 | 494 | 528.4 | 515 | 553.6 | 522.8 | 527.4 | 467.4 | 508.2 | 483.8 | 442 | 486.2 | 486.2 | 450.2 | 373.2
|  | All Other | Other | 224.6 | 233.6 | 251.8 | 238.8 | 254 | 271.6 | 284.2 | 285.2 | 296.6 | 284.8 | 284.4 | 269.6 | 297.8 | 283.4 | 276.2 | 295.6 | 293.8 | 289.2 | 264.6
|  | COMBINED Energy & Ren/LM CREDITS |  |  |  | Requirement Ratio (Required Credits / Available Credits)
|  | Building Occupancy Group |  | Climate Zone
|  |  |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
|  | R-2, R-4, and I-1 | Apartment | 27.52% | 28.19% | 27.87% | 29.38% | 30.49% | 30.02% | 27.81% | 29.26% | 26.36% | 27.63% | 28.46% | 27.26% | 22.52% | 26.77% | 26.81% | 19.67% | 24.39% | 22.28% | 22.59%
|  | I-2 | Health | 50.3% | 49.92% | 49.14% | 48.74% | 46.49% | 41.3% | 40.33% | 42.23% | 33.38% | 43.32% | 43.93% | 39.12% | 39.58% | 46.16% | 44.3% | 48.06% | 48.45% | 46.21% | 49.06%
|  | R-1 | Hotel | 49.31% | 49.67% | 48.7% | 50.97% | 52.63% | 49.26% | 53.01% | 53.57% | 50.2% | 49.65% | 54.15% | 55.45% | 49.39% | 54.14% | 54.95% | 46.51% | 50.92% | 46.82% | 47.64%
|  | B | Office | 54.64% | 52.06% | 52.76% | 53.57% | 53.83% | 54.76% | 52.41% | 51.9% | 52.13% | 52.1% | 55.03% | 55.93% | 50.74% | 53.86% | 55.06% | 50.74% | 50.68% | 46.98% | 47.71%
|  | A-2 | Restaurant | 50.32% | 52.14% | 49.27% | 52.33% | 47% | 51.79% | 42.52% | 49.59% | 51.69% | 38.42% | 48.3% | 47.75% | 34.44% | 42.71% | 48.28% | 30.14% | 36.47% | 28.81% | 27.72%
|  | M | Retail | 55.01% | 50.41% | 50.65% | 50.04% | 49.59% | 51.21% | 38.19% | 43.94% | 48.69% | 36.43% | 40.85% | 36.16% | 34.03% | 34.43% | 30.2% | 31.88% | 32.46% | 33.66% | 32.43%
|  | E | Education | 44.77% | 42.25% | 40.86% | 42.41% | 42.06% | 40.59% | 39.95% | 41.84% | 41.08% | 40.97% | 41.75% | 39.42% | 40.09% | 38.8% | 43.24% | 39.37% | 39.58% | 36.67% | 34.18%
|  | S-1 and S-2 | Warehouse | 40.06% | 36.73% | 30.51% | 33.68% | 31.22% | 29.76% | 25.36% | 27.96% | 27.46% | 33.47% | 29.96% | 35.3% | 35.42% | 35.55% | 36.65% | 35.79% | 35.99% | 35.76% | 38.59%
|  | All Other | Other | 29.39% | 29.97% | 30.58% | 30.99% | 30.71% | 31.3% | 27.8% | 30.86% | 31.02% | 26.33% | 30.59% | 28.56% | 24.85% | 28.23% | 28.96% | 24.36% | 25.87% | 23.51% | 23.43%
BASE ENERGY CREDITS FOR GROUP R-2, R-4, AND I-1 OCCUPANCIESa
| Multifamily |  |  | Climate Zone
| ID | Energy Credit Measure | Section | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8 | Available Credit Multipliers (All Building Use Groups)
| E01 | Envelope Performance | C406.2.1.1 | Determined in accordance with Section C406.2.1.1 | [18 empty] | 0 | Exclusive of E02-E06
| E02 | UA reduction (15%) | C406.2.1.2 | 7 | 6 | 2 | 4 | 1 | 1 | 4 | 1 | 1 | 22 | 1 | 3 | 29 | 10 | 1 | 32 | 27 | 30 | 39 | 1
| E03 | Envelope leakage reduction | C406.2.1.3 | 15 | 10 | 12 | 8 | 6 | 16 | 13 | 5 | 1 | 7 | 7 | 9 | 65 | 16 | 11 | 73 | 43 | 52 | 26 | 1
| E04 | Add Roof Insulation | C406.2.1.4 | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 3 | 1 | 5 | 3 | 4 | 6 | 5 | 4 | 7 | 7 | 6 | 8 | 0 | Exclusive of E01-E03
| E05 | Add Wall Insulation | C406.2.1.5 | 10 | 10 | 6 | 8 | 5 | 6 | 8 | 4 | 1 | 8 | 3 | 4 | 11 | 7 | 3 | 14 | 12 | 13 | 13 | 0 | Exclusive of E01-E03
| E06 | Improve Fenestration | C406.2.1.6 | 7 | 7 | 4 | 6 | 9 | 11 | 13 | 3 | 1 | 22 | 5 | 10 | 27 | 18 | 7 | 41 | 33 | 22 | 21 | 0 | Exclusive of E01-E03
| H01 | HVAC Performance | C406.2.2.1 | 20 | 19 | 16 | 17 | 14 | 13 | 11 | 11 | 5 | 13 | 10 | 8 | 15 | 12 | 7 | 18 | 14 | 17 | 19 | 0 | Exclusive of H02-H03, H05
| H02 | Heating efficiency | C406.2.2.2 | x | x | x | x | x | x | 3 | 1 | 1 | 6 | 2 | 3 | 10 | 5 | 2 | 14 | 10 | 13 | 16 | 3 | 15% eff improve
| H03 | Cooling efficiency | C406.2.2.3 | 7 | 6 | 4 | 4 | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | x | x | x | x | x | 3 | 15% eff improve
| H04 | Residential HVAC control | C406.2.2.4 | 9 | 10 | 8 | 22 | 20 | 25 | 16 | 17 | 32 | 21 | 24 | 17 | 23 | 27 | 16 | 21 | 24 | 18 | 18 | 1
| H05 | DOAS/fan control | C406.2.2.5 | 32 | 31 | 27 | 28 | 23 | 23 | 28 | 21 | 12 | 42 | 24 | 24 | 56 | 36 | 19 | 73 | 54 | 70 | 79 | 0 | Limited Applicability
| W01 | SHW preheat recovery | C406.2.3.1 | 61 | 63 | 74 | 74 | 85 | 88 | 101 | 100 | 121 | 103 | 109 | 122 | 102 | 111 | 130 | 93 | 106 | 99 | 96 | 0 | Limited to CHW sys
| W02 | Heat pump water heater | C406.2.3.1 | 50 | 52 | 62 | 61 | 72 | 74 | 86 | 85 | 104 | 88 | 94 | 106 | 88 | 96 | 112 | 81 | 92 | 87 | 84 | 1 | 30% load
| W03 | Efficient gas water heater | C406.2.3.1 | 38 | 39 | 46 | 46 | 53 | 55 | 63 | 62 | 76 | 64 | 68 | 76 | 64 | 69 | 81 | 58 | 66 | 62 | 60 | 0.6 | 60% load
| W04 | SHW pipe insulation | C406.2.3.2 | 7 | 7 | 8 | 7 | 8 | 8 | 8 | 9 | 10 | 8 | 9 | 9 | 7 | 8 | 9 | 6 | 7 | 6 | 6 | 1
| W05 | Point of use water heaters | C406.2.3.3 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | 0 | Alt to other SHW, limited
| W06 | Thermostatic bal. valves | C406.2.3.3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 3 | 3 | 4 | 3 | 3 | 4 | 3 | 3 | 3 | 2 | 0 | Only Recirc; alt to Trace
| W07 | SHW heat trace system | C406.2.3.3 | 12 | 12 | 13 | 13 | 14 | 15 | 15 | 15 | 18 | 14 | 15 | 16 | 13 | 14 | 16 | 11 | 13 | 11 | 10 | 1
| W08 | SHW submeters | C406.2.3.4 | 11 | 11 | 13 | 13 | 15 | 16 | 18 | 18 | 22 | 19 | 20 | 22 | 19 | 20 | 24 | 17 | 20 | 18 | 18 | 0 | Limited and high cost
| W09 | SHW flow reduction | C406.2.3.5 | 22 | 22 | 27 | 26 | 31 | 32 | 37 | 37 | 45 | 38 | 40 | 45 | 38 | 41 | 48 | 35 | 39 | 37 | 36 | 1
| W10 | Shower heat recovery | C406.2.3.6 | 15 | 16 | 19 | 19 | 22 | 23 | 26 | 26 | 32 | 27 | 29 | 32 | 27 | 29 | 34 | 25 | 28 | 27 | 26 | 1
| P01 | Energy monitoring | C406.2.4 | 3 | 3 | 2 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 2 | 2 | 3 | 1
| L01 | Lighting Performance | C406.2.5.1 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | 0 | Not available
| L02 | Lighting dimming & tuning | C406.2.5.2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| L03 | Increase occp. sensor | C406.2.5.3 | 3 | 3 | 4 | 4 | 4 | 4 | 3 | 4 | 3 | 2 | 3 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1
| L04 | Increase daylight area | C406.2.5.4 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 4 | 4 | 4 | 4 | 3 | 3 | 4 | 3 | 2 | 3 | 3 | 2 | 1
| L05 | Residential light control | C406.2.5.5 | 8 | 8 | 9 | 9 | 9 | 9 | 8 | 8 | 10 | 6 | 8 | 7 | 4 | 6 | 8 | 3 | 5 | 4 | 3 | 1
| L06 | Light power reduction | C406.2.5.7 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 3 | 15% reduction
| Q01 | Efficient elevator | C406.2.7.1 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 4 | 5 | 5 | 4 | 4 | 5 | 4 | 4 | 4 | 3 | 1
| Q02 | Commercial kitchen equip. | C406.2.7.2 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | 1
| Q03 | Residential kitchen equip. | C406.2.7.3 | 15 | 15 | 17 | 16 | 17 | 18 | 17 | 18 | 20 | 16 | 17 | 18 | 15 | 16 | 18 | 13 | 15 | 13 | 12 | 1
| Q04 | Fault detection | C406.2.7.4 | 3 | 3 | 2 | 3 | 2 | 2 | 2 | 2 | 1 | 2 | 2 | 1 | 1 | 2 | 1 | 3 | 2 | 3 | 3 | 1
| RENEWABLE AND LOAD MANAGEMENT CREDITS FOR GROUP R-2, R-4, AND I-1 OCCUPANCIES | [20 empty] | Multifamily
| ID | Energy Credit Abbreviated Title | Section | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
| R01 | Renewable Energy | C406.3.1 | 9 | 15 | 11 | 17 | 18 | 20 | 19 | 21 | 13 | 10 | 13 | 9 | 9 | 11 | 10 | 9 | 10 | 9 | 7 | 5 | 0.5 W/sf PV
| G01 | Lighting load management | C406.3.2 | 16 | 7 | 9 | 12 | 12 | 16 | 11 | 14 | 12 | 11 | 16 | 14 | 8 | 11 | 14 | 5 | 7 | 7 | 11 | 1
| G02 | HVAC load management | C406.3.3 | 42 | 41 | 21 | 35 | 23 | 37 | 30 | 28 | 28 | 17 | 33 | 24 | 20 | 22 | 23 | 10 | 13 | 15 | 17 | 1
| G03 | Automated shading | C406.3.4 | 11 | 1 | 7 | 18 | 10 | 13 | 5 | 13 | 12 | 2 | 14 | 7 | 10 | 13 | 11 | 1 | 8 | 8 | 16 | 1
| G04 | Electric energy storage | C406.3.5 | 10 | 10 | 10 | 11 | 10 | 13 | 13 | 14 | 17 | 16 | 13 | 17 | 14 | 13 | 17 | 14 | 14 | 14 | 15 | 0 | High Cost
| G05 | Cooling energy storage | C406.3.6 | 28 | 6 | 31 | 13 | 22 | 21 | 21 | 37 | 11 | 12 | 22 | 11 | 9 | 17 | 9 | 7 | 17 | 2 | 3 | 0 | Limited to CHW sys
| G06 | SHW energy storage | C406.3.7 | 17 | 17 | 19 | 18 | 19 | 19 | 20 | 20 | 22 | 19 | 19 | 21 | 19 | 19 | 20 | 18 | 19 | 18 | 17 | 1
| G07 | Building thermal mass | C406.3.8 | 7 | 2 | 11 | 5 | 16 | 28 | 22 | 27 | 60 | 19 | 43 | 46 | 32 | 58 | 37 | 27 | 45 | 40 | 19 | 0 | Limited to Masonry structure
BASE ENERGY CREDITS FOR GROUP I-2 OCCUPANCIESa
| Healthcare |  |  | Climate Zone
| ID | Energy Credit Measure | Section | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
| E01 | Envelope Performance | C406.2.1.1 | Determined in accordance with Section C406.2.1.1
| E02 | UA reduction (15%) | C406.2.1.2 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 3 | 1 | 3 | 11 | 27 | 7 | 10 | 3 | 3 | 2 | 10
| E03 | Envelope leakage reduction | C406.2.1.3 | 5 | 3 | 4 | 3 | 5 | 8 | 8 | 3 | 2 | 6 | 2 | 2 | 7 | 3 | 1 | 9 | 7 | 19 | 5
| E04 | Add Roof Insulation | C406.2.1.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 2 | 1 | 2 | 3
| E05 | Add Wall Insulation | C406.2.1.5 | 1 | 3 | 1 | 3 | 2 | 2 | 9 | 4 | 1 | 4 | 1 | 1 | 3 | 1 | 1 | 3 | 3 | 3 | 3
| E06 | Improve Fenestration | C406.2.1.6 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 4 | 3 | 5 | 5 | 1 | 1 | 5 | 5 | 2 | 2
| H01 | HVAC Performance | C406.2.2.1 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| H02 | Heating efficiency | C406.2.2.2 | x | x | x | x | 2 | 3 | 4 | 3 | 7 | 6 | 4 | 6 | 8 | 6 | 10 | 11 | 12 | 15 | 19
| H03 | Cooling efficiency | C406.2.2.3 | 6 | 6 | 4 | 4 | 3 | 3 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | x | x | x | x
| H04 | Residential HVAC control | C406.2.2.4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| H05 | DOAS/fan control | C406.2.2.5 | 41 | 41 | 40 | 40 | 42 | 36 | 42 | 37 | 39 | 49 | 40 | 46 | 56 | 46 | 61 | 65 | 68 | 82 | 93
| W01 | SHW preheat recovery | C406.2.3.1 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 5 | 5 | 5
| W02 | Heat pump water heater | C406.2.3.1 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| W03 | Efficient gas water heater | C406.2.3.1 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| W04 | SHW pipe insulation | C406.2.3.2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| W05 | Point of use water heaters | C406.2.3.3 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| W06 | Thermostatic bal. valves | C406.2.3.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| W07 | SHW heat trace system | C406.2.3.3 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1
| W08 | SHW submeters | C406.2.3.4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| W09 | SHW flow reduction | C406.2.3.5 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| W10 | Shower heat recovery | C406.2.3.6 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| P01 | Energy monitoring | C406.2.4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| L01 | Lighting Performance | C406.2.5.1 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| L02 | Lighting dimming & tuning | C406.2.5.2 | 5 | 5 | 5 | 5 | 5 | 6 | 5 | 6 | 6 | 5 | 6 | 6 | 5 | 5 | 5 | 4 | 4 | 3 | 2
| L03 | Increase occp. sensor | C406.2.5.3 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 5 | 5 | 6 | 5 | 5 | 5 | 4 | 4 | 3 | 2
| L04 | Increase daylight area | C406.2.5.4 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 8 | 6 | 6 | 6 | 6 | 6 | 5 | 5 | 5 | 5 | 4
| L05 | Residential light control | C406.2.5.5 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| L06 | Light power reduction | C406.2.5.7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 9 | 7 | 7 | 8 | 6 | 7 | 7 | 5 | 5 | 4 | 3
| Q01 | Efficient elevator | C406.2.7.1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1
| Q02 | Commercial kitchen equip. | C406.2.7.2 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| Q03 | Residential kitchen equip. | C406.2.7.3 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| Q04 | Fault detection | C406.2.7.4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 3 | 3 | 2 | 3 | 3 | 3 | 3 | 3 | 4 | 4
| RENEWABLE AND LOAD MANAGEMENT CREDITS FOR GROUP I-2 OCCUPANCIES | [20 empty] | Healthcare
| ID | Energy Credit Abbreviated Title | Section | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
| R01 | Renewable Energy | C406.3.1 | 6 | 6 | 6 | 6 | 6 | 8 | 7 | 9 | 8 | 6 | 8 | 6 | 6 | 7 | 7 | 6 | 7 | 5 | 4
| G01 | Lighting load management | C406.3.2 | 11 | 12 | 13 | 13 | 13 | 12 | 12 | 12 | 6 | 13 | 16 | 12 | 13 | 14 | 15 | 14 | 14 | 12 | 12
| G02 | HVAC load management | C406.3.3 | 10 | 11 | 10 | 10 | 8 | 21 | 10 | 10 | 13 | 11 | 18 | 11 | 12 | 14 | 13 | 12 | 11 | 9 | 7
| G03 | Automated shading | C406.3.4 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1
| G04 | Electric energy storage | C406.3.5 | 13 | 13 | 13 | 13 | 14 | 15 | 14 | 15 | 15 | 14 | 15 | 15 | 14 | 15 | 15 | 13 | 14 | 13 | 12
| G05 | Cooling energy storage | C406.3.6 | 25 | 6 | 33 | 14 | 25 | 19 | 27 | 37 | 27 | 16 | 22 | 19 | 14 | 18 | 11 | 11 | 20 | 2 | 3
| G06 | SHW energy storage | C406.3.7 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 4
| G07 | Building thermal mass | C406.3.8 | 6 | 2 | 10 | 4 | 15 | 25 | 20 | 24 | 57 | 18 | 39 | 44 | 31 | 53 | 33 | 25 | 40 | 34 | 14
BASE ENERGY CREDITS FOR GROUP R-1 OCCUPANICESa
| Hotel |  |  | Climate Zone
| ID | Energy Credit Measure | Section | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
| E01 | Envelope Performance | C406.2.1.1 | Determined in accordance with Section C406.2.1.1
| E02 | UA reduction (15%) | C406.2.1.2 | 2 | 3 | 1 | 2 | 1 | 3 | 3 | 2 | 1 | 5 | 2 | 2 | 7 | 4 | 2 | 9 | 7 | 9 | 11
| E03 | Envelope leakage reduction | C406.2.1.3 | 15 | 9 | 12 | 8 | 6 | 16 | 7 | 5 | 10 | 14 | 3 | 1 | 19 | 5 | 1 | 28 | 16 | 28 | 18
| E04 | Add Roof Insulation | C406.2.1.4 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 2 | 1 | 3 | 1 | 2 | 3 | 2 | 2 | 3 | 3 | 2 | 3
New | E05 | Add Wall Insulation | C406.2.1.5 | 13 | 14 | 8 | 11 | 4 | 4 | 7 | 4 | 1 | 5 | 2 | 4 | 6 | 4 | 3 | 9 | 7 | 8 | 8
| E06 | Improve Fenestration | C406.2.1.6 | 5 | 5 | 4 | 5 | 7 | 7 | 8 | 2 | 1 | 8 | 2 | 4 | 10 | 5 | 1 | 13 | 8 | 6 | 9
| H01 | HVAC Performance | C406.2.2.1 | 21 | 20 | 17 | 18 | 16 | 13 | 12 | 12 | 11 | 11 | 11 | 8 | 11 | 11 | 8 | 13 | 11 | 14 | 16
| H02 | Heating efficiency | C406.2.2.2 | x | x | x | x | x | x | 1 | 1 | 6 | 2 | 1 | 1 | 3 | 2 | 2 | 6 | 4 | 8 | 11
| H03 | Cooling efficiency | C406.2.2.3 | 7 | 6 | 4 | 4 | 3 | 2 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | x | x | x | x
| H04 | Residential HVAC control | C406.2.2.4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| H05 | DOAS/fan control | C406.2.2.5 | 32 | 30 | 26 | 28 | 25 | 23 | 24 | 22 | 28 | 26 | 22 | 20 | 30 | 26 | 19 | 41 | 34 | 48 | 62
| W01 | SHW preheat recovery | C406.2.3.1 | 18 | 19 | 22 | 22 | 25 | 27 | 31 | 21 | 32 | 34 | 34 | 38 | 37 | 36 | 40 | 36 | 37 | 36 | 35
| W02 | Heat pump water heater | C406.2.3.1 | 14 | 15 | 18 | 17 | 20 | 22 | 25 | 25 | 27 | 29 | 29 | 32 | 31 | 31 | 34 | 30 | 32 | 31 | 30
| W03 | Efficient gas water heater | C406.2.3.1 | 11 | 12 | 14 | 14 | 16 | 17 | 19 | 19 | 20 | 21 | 21 | 24 | 23 | 23 | 25 | 22 | 23 | 23 | 22
| W04 | SHW pipe insulation | C406.2.3.2 | 3 | 3 | 4 | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 3
| W05 | Point of use water heaters | C406.2.3.3 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| W06 | Thermostatic bal. valves | C406.2.3.3 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1
| W07 | SHW heat trace system | C406.2.3.3 | 5 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 8 | 7 | 7 | 8 | 7 | 7 | 6 | 6
| W08 | SHW submeters | C406.2.3.4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| W09 | SHW flow reduction | C406.2.3.5 | 6 | 7 | 8 | 8 | 9 | 10 | 11 | 11 | 12 | 13 | 13 | 14 | 14 | 13 | 15 | 13 | 14 | 14 | 13
| W10 | Shower heat recovery | C406.2.3.6 | 4 | 5 | 5 | 5 | 6 | 7 | 8 | 8 | 8 | 9 | 9 | 10 | 10 | 9 | 10 | 9 | 10 | 10 | 9
| P01 | Energy monitoring | C406.2.4 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| L01 | Lighting Performance | C406.2.5.1 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| L02 | Lighting dimming & tuning | C406.2.5.2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| L03 | Increase occp. sensor | C406.2.5.3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 2 | 3 | 2 | 2 | 3 | 2 | 2 | 1 | 1
| L04 | Increase daylight area | C406.2.5.4 | 4 | 5 | 5 | 4 | 5 | 5 | 4 | 4 | 4 | 5 | 4 | 4 | 3 | 4 | 3 | 3 | 3 | 3 | 2
| L05 | Residential light control | C406.2.5.5 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| L06 | Light power reduction | C406.2.5.7 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 1
| Q01 | Efficient elevator | C406.2.7.1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2
| Q02 | Commercial kitchen equip. | C406.2.7.2 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| Q03 | Residential kitchen equip. | C406.2.7.3 | 9 | 9 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 11 | 11 | 12 | 10 | 11 | 10 | 9
| Q04 | Fault detection | C406.2.7.4 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 2 | 2 | 2 | 2
| RENEWABLE AND LOAD MANAGEMENT CREDITS FOR GROUP R-1 OCCUPANCIES | [20 empty] | Hotel
| ID | Energy Credit Abbreviated Title | Section | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
| R01 | Renewable Energy | C406.3.1 | 9 | 8 | 12 | 9 | 11 | 11 | 10 | 12 | 13 | 9 | 12 | 8 | 9 | 11 | 9 | 8 | 9 | 7 | 5
| G01 | Lighting load management | C406.3.2 | 12 | 12 | 11 | 12 | 12 | 14 | 14 | 13 | 15 | 14 | 13 | 11 | 10 | 11 | 14 | 9 | 11 | 8 | 8
| G02 | HVAC load management | C406.3.3 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| G03 | Automated shading | C406.3.4 | 2 | 2 | 2 | 3 | 1 | 2 | 3 | 2 | 4 | 3 | 2 | 1 | 1 | 1 | 3 | 1 | 2 | 1 | 1
| G04 | Electric energy storage | C406.3.5 | 9 | 9 | 10 | 10 | 9 | 13 | 13 | 15 | 13 | 14 | 13 | 14 | 14 | 12 | 16 | 13 | 12 | 12 | 13
| G05 | Cooling energy storage | C406.3.6 | 31 | 7 | 38 | 17 | 29 | 24 | 31 | 44 | 26 | 18 | 26 | 16 | 15 | 21 | 11 | 12 | 24 | 2 | 4
| G06 | SHW energy storage | C406.3.7 | 25 | 25 | 28 | 26 | 28 | 29 | 29 | 30 | 31 | 29 | 30 | 31 | 28 | 29 | 31 | 26 | 28 | 25 | 24
| G07 | Building thermal mass | C406.3.8 | 6 | 1 | 10 | 4 | 14 | 24 | 19 | 23 | 53 | 17 | 38 | 41 | 30 | 52 | 33 | 26 | 42 | 37 | 17
BASE ENERGY CREDITS FOR GROUP B OCCUPANCIESa
| Office |  |  | Climate Zone
| ID | Energy Credit Measure | Section | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
| E01 | Envelope Performance | C406.2.1.1 | Determined in accordance with Section C406.2.1.1
| E02 | UA reduction (15%) | C406.2.1.2 | 7 | 8 | 3 | 6 | 5 | 3 | 7 | 3 | 1 | 13 | 4 | 8 | 21 | 15 | 11 | 13 | 24 | 37 | 43
| E03 | Envelope leakage reduction | C406.2.1.3 | 5 | 3 | 4 | 2 | 2 | 2 | 5 | 1 | 1 | 8 | 1 | 2 | 13 | 4 | 1 | 18 | 9 | 18 | 7
| E04 | Add Roof Insulation | C406.2.1.4 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 2 | 1 | 3 | 1 | 2 | 3 | 2 | 2 | 3 | 3 | 2 | 3
| E05 | Add Wall Insulation | C406.2.1.5 | 13 | 14 | 8 | 11 | 4 | 4 | 7 | 4 | 1 | 5 | 2 | 4 | 6 | 4 | 3 | 9 | 7 | 10 | 8
| E06 | Improve Fenestration | C406.2.1.6 | 5 | 5 | 4 | 5 | 7 | 7 | 8 | 2 | 1 | 8 | 2 | 4 | 10 | 5 | 1 | 21 | 17 | 10 | 9
| H01 | HVAC Performance | C406.2.2.1 | 22 | 22 | 19 | 20 | 17 | 17 | 15 | 15 | 11 | 15 | 15 | 11 | 16 | 15 | 11 | 19 | 17 | 18 | 20
| H02 | Heating efficiency | C406.2.2.2 | x | x | x | x | x | x | 1 | 1 | 1 | 3 | 2 | 2 | 5 | 4 | 3 | 9 | 7 | 8 | 12
| H03 | Cooling efficiency | C406.2.2.3 | 7 | 6 | 4 | 5 | 3 | 3 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | x | x | x | x
| H04 | Residential HVAC control | C406.2.2.4 | X | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| H05 | DOAS/fan control | C406.2.2.5 | 31 | 31 | 27 | 29 | 25 | 25 | 28 | 26 | 18 | 35 | 28 | 28 | 47 | 38 | 29 | 64 | 53 | 58 | 74
| W01 | SHW preheat recovery | C406.2.3.1 | 8 | 9 | 10 | 9 | 11 | 11 | 12 | 12 | 14 | 13 | 13 | 14 | 13 | 13 | 15 | 12 | 13 | 14 | 14
| W02 | Heat pump water heater | C406.2.3.1 | 3 | 3 | 3 | 3 | 4 | 4 | 5 | 4 | 5 | 5 | 5 | 6 | 5 | 5 | 6 | 5 | 5 | 6 | 6
| W03 | Efficient gas water heater | C406.2.3.1 | 5 | 5 | 6 | 6 | 7 | 7 | 8 | 7 | 8 | 8 | 8 | 9 | 8 | 8 | 9 | 8 | 8 | 9 | 8
| W04 | SHW pipe insulation | C406.2.3.2 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 4 | 4 | 5 | 4 | 4 | 5 | 4 | 4 | 4 | 4
| W05 | Point of use water heaters | C406.2.3.3 | 12 | 15 | 17 | 16 | 18 | 18 | 19 | 19 | 22 | 20 | 20 | 22 | 20 | 20 | 22 | 18 | 19 | 20 | 19
| W06 | Thermostatic bal. valves | C406.2.3.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| W07 | SHW heat trace system | C406.2.3.3 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 6 | 5 | 5 | 6 | 5 | 5 | 6 | 5 | 5 | 5 | 5
| W08 | SHW submeters | C406.2.3.4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| W09 | SHW flow reduction | C406.2.3.5 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| W10 | Shower heat recovery | C406.2.3.6 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| P01 | Energy monitoring | C406.2.4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
| L01 | Lighting Performance | C406.2.5.1 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| L02 | Lighting dimming & tuning | C406.2.5.2 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 7 | 6 | 6 | 6 | 5 | 5 | 6 | 4 | 5 | 3 | 2
| L03 | Increase occp. sensor | C406.2.5.3 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 8 | 6 | 6 | 6 | 5 | 5 | 6 | 4 | 5 | 4 | 3
| L04 | Increase daylight area | C406.2.5.4 | 7 | 7 | 8 | 8 | 8 | 8 | 8 | 8 | 9 | 6 | 7 | 7 | 6 | 6 | 6 | 6 | 6 | 7 | 5
| L05 | Residential light control | C406.2.5.5 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| L06 | Light power reduction | C406.2.5.7 | 7 | 7 | 8 | 8 | 8 | 8 | 8 | 8 | 9 | 7 | 8 | 8 | 6 | 7 | 8 | 5 | 6 | 5 | 3
| Q01 | Efficient elevator | C406.2.7.1 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 5 | 4 | 4
| Q02 | Commercial kitchen equip. | C406.2.7.2 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| Q03 | Residential kitchen equip. | C406.2.7.3 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| Q04 | Fault detection | C406.2.7.4 | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3
| RENEWABLE AND LOAD MANAGEMENT CREDITS FOR GROUP B OCCUPANCIES | [20 empty] | Office
| ID | Energy Credit Abbreviated Title | Section | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
| R01 | Renewable Energy | C406.3.1 | 14 | 14 | 17 | 15 | 17 | 19 | 18 | 22 | 24 | 17 | 22 | 16 | 14 | 18 | 18 | 14 | 17 | 14 | 11
| G01 | Lighting load management | C406.3.2 | 10 | 11 | 11 | 12 | 11 | 11 | 11 | 12 | 9 | 10 | 11 | 10 | 10 | 11 | 10 | 10 | 11 | 10 | 9
| G02 | HVAC load management | C406.3.3 | x | 10 | 10 | 9 | 9 | 3 | 8 | 12 | 7 | 12 | 8 | 11 | 9 | 10 | 12 | 8 | 9 | 10 | 2
| G03 | Automated shading | C406.3.4 | 4 | 7 | 7 | 8 | 7 | 8 | 5 | 6 | 6 | 4 | 6 | 5 | 4 | 5 | 5 | 5 | 5 | 4 | 7
| G04 | Electric energy storage | C406.3.5 | 14 | 15 | 14 | 14 | 16 | 16 | 17 | 16 | 18 | 17 | 16 | 18 | 17 | 17 | 18 | 16 | 15 | 17 | 18
| G05 | Cooling energy storage | C406.3.6 | 28 | 7 | 36 | 16 | 27 | 24 | 28 | 45 | 27 | 17 | 27 | 15 | 15 | 20 | 9 | 12 | 25 | 2 | 4
| G06 | SHW energy storage | C406.3.7 | 5 | 5 | 6 | 6 | 6 | 6 | 7 | 7 | 8 | 7 | 7 | 7 | 7 | 7 | 8 | 6 | 7 | 6 | 6
| G07 | Building thermal mass | C406.3.8 | 3 | 1 | 5 | 2 | 6 | 9 | 6 | 7 | 14 | 4 | 11 | 8 | 9 | 15 | 5 | 8 | 12 | 15 | 7
BASE ENERGY CREDITS FOR GROUP A-2 OCCUPANCIESa
| Restaurant |  |  | Climate Zone
| ID | Energy Credit Measure | Section | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
| E01 | Envelope Performance | C406.2.1.1 | Determined in accordance with Section C406.2.1.1
| E02 | UA reduction (15%) | C406.2.1.2 | 1 | 1 | 1 | 1 | 13 | 1 | 3 | 2 | 1 | 4 | 4 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6
| E03 | Envelope leakage reduction | C406.2.1.3 | 2 | 1 | 1 | 1 | 2 | 3 | 11 | 2 | 1 | 24 | 4 | 6 | 33 | 9 | 3 | 42 | 29 | 36 | 16
| E04 | Add Roof Insulation | C406.2.1.4 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 2 | 2 | 1 | 2
| E05 | Add Wall Insulation | C406.2.1.5 | 1 | 1 | 1 | 1 | 1 | 2 | 3 | 3 | 1 | 2 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| E06 | Improve Fenestration | C406.2.1.6 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 2 | 2 | 3 | 2 | 1 | 4 | 4 | 1 | 1
| H01 | HVAC Performance | C406.2.2.1 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| H02 | Heating efficiency | C406.2.2.2 | x | x | x | x | 1 | 1 | 6 | 3 | 3 | 10 | 6 | 8 | 15 | 11 | 10 | 19 | 15 | 23 | 28
| H03 | Cooling efficiency | C406.2.2.3 | 6 | 5 | 3 | 4 | 3 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | x | x | x | x
| H04 | Residential HVAC control | C406.2.2.4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| H05 | DOAS/fan control | C406.2.2.5 | 29 | 27 | 20 | 25 | 24 | 21 | 36 | 27 | 15 | 51 | 35 | 38 | 67 | 53 | 45 | 84 | 70 | 97 | 115
| W01 | SHW preheat recovery | C406.2.3.1 | 24 | 26 | 31 | 29 | 33 | 35 | 37 | 38 | 45 | 38 | 41 | 44 | 37 | 40 | 44 | 34 | 38 | 33 | 30
| W02 | Heat pump water heater | C406.2.3.1 | 15 | 16 | 19 | 18 | 21 | 23 | 25 | 25 | 29 | 26 | 28 | 30 | 26 | 28 | 31 | 25 | 27 | 24 | 22
| W03 | Efficient gas water heater | C406.2.3.1 | 15 | 16 | 19 | 18 | 21 | 22 | 23 | 24 | 28 | 24 | 25 | 27 | 23 | 25 | 27 | 21 | 24 | 21 | 18
| W04 | SHW pipe insulation | C406.2.3.2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 3 | 3 | 2 | 2 | 2 | 2
| W05 | Point of use water heaters | C406.2.3.3 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| W06 | Thermostatic bal. valves | C406.2.3.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| W07 | SHW heat trace system | C406.2.3.3 | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 3 | 4 | 4 | 3 | 3 | 3 | 3
| W08 | SHW submeters | C406.2.3.4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| W09 | SHW flow reduction | C406.2.3.5 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| W10 | Shower heat recovery | C406.2.3.6 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| P01 | Energy monitoring | C406.2.4 | 2 | 2 | 2 | 2 | 2 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 2 | 2 | 1 | 2 | 2 | 2 | 3
| L01 | Lighting Performance | C406.2.5.1 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| L02 | Lighting dimming & tuning | C406.2.5.2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 2 | 1 | 1 | 1 | 1 | 1
| L03 | Increase occp. sensor | C406.2.5.3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| L04 | Increase daylight area | C406.2.5.4 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 2 | 1 | 1 | 1 | 1 | 1
| L05 | Residential light control | C406.2.5.5 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| L06 | Light power reduction | C406.2.5.7 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 2 | 1 | 1
| Q01 | Efficient elevator | C406.2.7.1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| Q02 | Commercial kitchen equip. | C406.2.7.2 | 24 | 26 | 28 | 27 | 28 | 29 | 27 | 29 | 32 | 26 | 28 | 29 | 24 | 26 | 28 | 21 | 23 | 19 | 17
| Q03 | Residential kitchen equip. | C406.2.7.3 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| Q04 | Fault detection | C406.2.7.4 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 2 | 2 | 1 | 2 | 2 | 2 | 3 | 2 | 3 | 4
| RENEWABLE AND LOAD MANAGEMENT CREDITS FOR GROUP A-2 OCCUPANCIES | [20 empty] | Restaurant
| ID | Energy Credit Abbreviated Title | Section | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
| R01 | Renewable Energy | C406.3.1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 4 | 2 | 3 | 2 | 2 | 3 | 2 | 2 | 2 | 2 | 1
| G01 | Lighting load management | C406.3.2 | 4 | 4 | 5 | 5 | 4 | 5 | 5 | 5 | 5 | 4 | 5 | 5 | 4 | 4 | 5 | 4 | 5 | 4 | 1
| G02 | HVAC load management | C406.3.3 | 32 | 26 | 37 | 28 | 31 | 26 | 27 | 22 | 23 | 20 | 17 | 14 | 19 | 14 | 10 | 16 | 14 | 14 | 1
| G03 | Automated shading | C406.3.4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| G04 | Electric energy storage | C406.3.5 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 4 | 4 | 4 | 4 | 3 | 4 | 4 | 4 | 3 | 3 | 2
| G05 | Cooling energy storage | C406.3.6 | 15 | 4 | 17 | 8 | 12 | 10 | 10 | 16 | 6 | 5 | 7 | 3 | 3 | 4 | 1 | 2 | 4 | x | x
| G06 | SHW energy storage | C406.3.7 | 13 | 13 | 15 | 14 | 15 | 16 | 16 | 17 | 19 | 16 | 17 | 19 | 16 | 17 | 18 | 15 | 16 | 14 | 13
| G07 | Building thermal mass | C406.3.8 | 3 | 1 | 5 | 2 | 7 | 12 | 8 | 10 | 21 | 6 | 15 | 14 | 8 | 18 | 10 | 6 | 12 | 8 | 3
BASE ENERGY CREDITS FOR GROUP M OCCUPANCIES
| Retail |  |  | Climate Zone
| ID | Energy Credit Measure | Section | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
| E01 | Envelope Performance | C406.2.1.1 | Determined in accordance with Section C406.2.1.1
| E02 | UA reduction (15%) | C406.2.1.2 | 14 | 14 | 8 | 13 | 7 | 9 | 20 | 15 | 1 | 35 | 18 | 28 | 41 | 37 | 40 | 43 | 44 | 46 | 31
| E03 | Envelope leakage reduction | C406.2.1.3 | 3 | 3 | 2 | 2 | 3 | 3 | 19 | 3 | 1 | 44 | 6 | 11 | 56 | 13 | 6 | 64 | 44 | 43 | 19
| E04 | Add Roof Insulation | C406.2.1.4 | 8 | 6 | 5 | 7 | 7 | 7 | 18 | 16 | 4 | 19 | 18 | 20 | 21 | 22 | 23 | 24 | 26 | 24 | 30
| E05 | Add Wall Insulation | C406.2.1.5 | 64 | 65 | 48 | 62 | 13 | 15 | 23 | 18 | 4 | 27 | 21 | 27 | 25 | 24 | 25 | 23 | 24 | 24 | 16
| E06 | Improve Fenestration | C406.2.1.6 | 4 | 3 | 3 | 3 | 4 | 4 | 6 | 5 | 2 | 7 | 5 | 7 | 7 | 5 | 7 | 10 | 10 | 3 | 3
| H01 | HVAC Performance | C406.2.2.1 | 31 | 30 | 26 | 28 | 23 | 21 | 23 | 20 | 14 | 27 | 21 | 22 | 29 | 25 | 23 | 32 | 28 | 30 | 33
| H02 | Heating efficiency | C406.2.2.2 | x | x | x | x | x | x | 10 | 3 | 1 | 19 | 8 | 15 | 26 | 17 | 18 | 29 | 24 | 27 | 31
| H03 | Cooling efficiency | C406.2.2.3 | 10 | 9 | 7 | 7 | 5 | 4 | 2 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 1 | x | x | x | x
| H04 | Residential HVAC control | C406.2.2.4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| H05 | DOAS/fan control | C406.2.2.5 | 48 | 48 | 42 | 47 | 40 | 38 | 66 | 46 | 31 | 98 | 61 | 82 | 120 | 91 | 90 | 134 | 115 | 125 | 141
| W01 | SHW preheat recovery | C406.2.3.1 | 12 | 13 | 16 | 15 | 18 | 20 | 19 | 21 | 26 | 17 | 21 | 21 | 16 | 19 | 21 | 13 | 16 | 15 | 13
| W02 | Heat pump water heater | C406.2.3.1 | 3 | 3 | 4 | 3 | 4 | 5 | 5 | 5 | 7 | 5 | 6 | 6 | 4 | 5 | 6 | 4 | 4 | 4 | 4
| W03 | Efficient gas water heater | C406.2.3.1 | 6 | 7 | 8 | 8 | 10 | 10 | 10 | 11 | 14 | 9 | 11 | 11 | 8 | 10 | 11 | 7 | 8 | 8 | 7
| W04 | SHW pipe insulation | C406.2.3.2 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 4 | 4 | 5 | 4 | 4 | 5 | 4 | 4 | 4 | 4
| W05 | Point of use water heaters | C406.2.3.3 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | 0
| W06 | Thermostatic bal. valves | C406.2.3.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| W07 | SHW heat trace system | C406.2.3.3 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 6 | 5 | 5 | 6 | 5 | 5 | 6 | 5 | 5 | 5 | 5
| W08 | SHW submeters | C406.2.3.4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| W09 | SHW flow reduction | C406.2.3.5 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| W10 | Shower heat recovery | C406.2.3.6 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| P01 | Energy monitoring | C406.2.4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
| L01 | Lighting Performance | C406.2.5.1 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| L02 | Lighting dimming & tuning | C406.2.5.2 | 9 | 9 | 11 | 10 | 12 | 13 | 11 | 13 | 15 | 9 | 12 | 11 | 7 | 9 | 10 | 5 | 7 | 5 | 3
| L03 | Increase occp. sensor | C406.2.5.3 | 9 | 9 | 11 | 10 | 12 | 13 | 12 | 13 | 15 | 10 | 12 | 11 | 7 | 10 | 11 | 6 | 8 | 5 | 4
| L04 | Increase daylight area | C406.2.5.4 | 12 | 13 | 15 | 14 | 16 | 17 | 15 | 16 | 20 | 11 | 14 | 13 | 9 | 12 | 11 | 8 | 10 | 10 | 8
| L05 | Residential light control | C406.2.5.5 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| L06 | Light power reduction | C406.2.5.7 | 12 | 12 | 14 | 14 | 15 | 16 | 12 | 15 | 19 | 8 | 12 | 9 | 6 | 10 | 7 | 6 | 7 | 6 | 5
| Q01 | Efficient elevator | C406.2.7.1 | 3 | 3 | 4 | 3 | 4 | 4 | 4 | 4 | 5 | 3 | 4 | 4 | 3 | 4 | 4 | 3 | 3 | 3 | 2
| Q02 | Commercial kitchen equip. | C406.2.7.2 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| Q03 | Residential kitchen equip. | C406.2.7.3 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| Q04 | Fault detection | C406.2.7.4 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 2 | 2 | 1 | 2 | 2 | 2 | 3 | 2 | 3 | 4
| RENEWABLE AND LOAD MANAGEMENT CREDITS FOR GROUP M OCCUPANCIES | [20 empty] | Retail
| ID | Energy Credit Abbreviated Title | Section | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
| R01 | Renewable Energy | C406.3.1 | 8 | 8 | 12 | 9 | 11 | 12 | 12 | 17 | 17 | 11 | 13 | 9 | 10 | 11 | 10 | 9 | 10 | 9 | 6
| G01 | Lighting load management | C406.3.2 | 16 | 16 | 18 | 19 | 17 | 19 | 19 | 21 | 17 | 18 | 21 | 21 | 18 | 21 | 22 | 18 | 22 | 18 | 16
| G02 | HVAC load management | C406.3.3 | x | 15 | 16 | 15 | 15 | 6 | 15 | 21 | 13 | 23 | 15 | 23 | 17 | 19 | 26 | 14 | 17 | 18 | 3
| G03 | Automated shading | C406.3.4 | 7 | 11 | 11 | 12 | 11 | 13 | 10 | 11 | 11 | 7 | 11 | 11 | 8 | 10 | 11 | 8 | 9 | 8 | 12
| G04 | Electric energy storage | C406.3.5 | 6 | 10 | 8 | 10 | 11 | 12 | 11 | 10 | 14 | 11 | 10 | 12 | 10 | 11 | 12 | 11 | 9 | 10 | 8
| G05 | Cooling energy storage | C406.3.6 | 40 | 9 | 51 | 22 | 35 | 31 | 34 | 53 | 21 | 17 | 28 | 10 | 11 | 19 | 4 | 9 | 18 | 2 | 2
| G06 | SHW energy storage | C406.3.7 | 3 | 3 | 4 | 3 | 4 | 4 | 4 | 4 | 5 | 4 | 4 | 5 | 4 | 4 | 5 | 4 | 4 | 4 | 3
| G07 | Building thermal mass | C406.3.8 | 5 | 1 | 6 | 3 | 8 | 12 | 10 | 10 | 20 | 7 | 17 | 15 | 14 | 24 | 10 | 13 | 20 | 24 | 12
BASE ENERGY CREDITS FOR GROUP E OCCUPANCIES
| School |  |  | Climate Zone
| ID | Energy Credit Measure | Section | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
| E01 | Envelope Performance | C406.2.1.1 | Determined in accordance with Section C406.2.1.1
| E02 | UA reduction (15%) | C406.2.1.2 | 8 | 18 | 7 | 19 | 12 | 13 | 20 | 17 | 11 | 24 | 20 | 17 | 33 | 32 | 29 | 40 | 38 | 46 | 44
| E03 | Envelope leakage reduction | C406.2.1.3 | 4 | 3 | 3 | 3 | 2 | 5 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 1
| E04 | Add Roof Insulation | C406.2.1.4 | 8 | 8 | 4 | 9 | 5 | 7 | 16 | 7 | 1 | 14 | 7 | 10 | 18 | 13 | 13 | 23 | 25 | 22 | 28
| E05 | Add Wall Insulation | C406.2.1.5 | 5 | 7 | 4 | 8 | 3 | 6 | 8 | 6 | 2 | 6 | 3 | 6 | 5 | 5 | 6 | 7 | 6 | 7 | 8
| E06 | Improve Fenestration | C406.2.1.6 | 8 | 10 | 6 | 9 | 11 | 11 | 15 | 9 | 1 | 16 | 8 | 15 | 22 | 18 | 19 | 33 | 29 | 19 | 18
| H01 | HVAC Performance | C406.2.2.1 | 30 | 28 | 25 | 26 | 23 | 21 | 20 | 18 | 15 | 19 | 18 | 17 | 19 | 20 | 15 | 23 | 20 | 25 | 29
| H02 | Heating efficiency | C406.2.2.2 | x | x | x | x | x | x | 4 | 3 | 3 | 5 | 5 | 10 | 9 | 11 | 6 | 15 | 11 | 18 | 26
| H03 | Cooling efficiency | C406.2.2.3 | 9 | 8 | 6 | 7 | 5 | 4 | 2 | 2 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | x | x | x | x
| H04 | Residential HVAC control | C406.2.2.4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| H05 | DOAS/fan control | C406.2.2.5 | 45 | 42 | 37 | 41 | 36 | 34 | 41 | 39 | 30 | 43 | 46 | 58 | 57 | 65 | 40 | 79 | 63 | 88 | 117
| W01 | SHW preheat recovery | C406.2.3.1 | 7 | 7 | 9 | 8 | 10 | 11 | 13 | 13 | 15 | 14 | 15 | 15 | 15 | 14 | 17 | 13 | 15 | 14 | 12
| W02 | Heat pump water heater | C406.2.3.1 | 4 | 4 | 6 | 5 | 7 | 7 | 9 | 9 | 10 | 10 | 10 | 11 | 11 | 10 | 12 | 10 | 11 | 10 | 9
| W03 | Efficient gas water heater | C406.2.3.1 | 4 | 4 | 6 | 5 | 6 | 7 | 8 | 8 | 9 | 9 | 9 | 10 | 9 | 9 | 11 | 8 | 10 | 9 | 7
| W04 | SHW pipe insulation | C406.2.3.2 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 5 | 6 | 5 | 5 | 6 | 5 | 5 | 7 | 4 | 5 | 4 | 4
| W05 | Point of use water heaters | C406.2.3.3 | 3 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 6 | 5 | 5 | 5 | 5 | 5 | 6 | 4 | 5 | 4 | 3
| W06 | Thermostatic bal. valves | C406.2.3.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 2 | 1 | 1
| W07 | SHW heat trace system | C406.2.3.3 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 6 | 7 | 6 | 6 | 7 | 6 | 6 | 8 | 5 | 7 | 5 | 5
| W08 | SHW submeters | C406.2.3.4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| W09 | SHW flow reduction | C406.2.3.5 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| W10 | Shower heat recovery | C406.2.3.6 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 4 | 3 | 3 | 4 | 3 | 3 | 4 | 3 | 3 | 3 | 3
| P01 | Energy monitoring | C406.2.4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4
| L01 | Lighting Performance | C406.2.5.1 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| L02 | Lighting dimming & tuning | C406.2.5.2 | 5 | 5 | 5 | 6 | 6 | 6 | 5 | 6 | 7 | 6 | 6 | 6 | 5 | 5 | 6 | 4 | 4 | 3 | 2
| L03 | Increase occp. sensor | C406.2.5.3 | 4 | 4 | 5 | 5 | 5 | 6 | 6 | 6 | 7 | 6 | 6 | 5 | 4 | 4 | 5 | 3 | 4 | 3 | 2
| L04 | Increase daylight area | C406.2.5.4 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 8 | 6 | 6 | 6 | 5 | 5 | 6 | 5 | 5 | 5 | 4
| L05 | Residential light control | C406.2.5.5 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| L06 | Light power reduction | C406.2.5.7 | 6 | 7 | 7 | 7 | 8 | 8 | 8 | 8 | 10 | 7 | 8 | 7 | 6 | 7 | 8 | 5 | 6 | 4 | 2
| Q01 | Efficient elevator | C406.2.7.1 | 3 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 5 | 4 | 3
| Q02 | Commercial kitchen equip. | C406.2.7.2 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| Q03 | Residential kitchen equip. | C406.2.7.3 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| Q04 | Fault detection | C406.2.7.4 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 2 | 3 | 3 | 3 | 3 | 3 | 2 | 4 | 3 | 4 | 4
| RENEWABLE AND LOAD MANAGEMENT CREDITS FOR GROUP E OCCUPANCIES | [20 empty] | School
| ID | Energy Credit Abbreviated Title | Section | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
| R01 | Renewable Energy | C406.3.1 | 10 | 11 | 13 | 12 | 13 | 16 | 15 | 21 | 22 | 15 | 19 | 15 | 14 | 17 | 16 | 13 | 16 | 12 | 10
| G01 | Lighting load management | C406.3.2 | 7 | 12 | 12 | 13 | 13 | 15 | 14 | 16 | 13 | 12 | 16 | 16 | 10 | 14 | 18 | 16 | 13 | 14 | 14
| G02 | HVAC load management | C406.3.3 | 18 | 22 | 32 | 23 | 25 | 31 | 26 | 26 | 20 | 23 | 31 | 24 | 20 | 31 | 12 | 18 | 27 | 16 | 9
| G03 | Automated shading | C406.3.4 | 7 | 13 | 16 | 12 | 18 | 17 | 17 | 18 | 13 | 12 | 17 | 17 | 10 | 15 | 13 | 14 | 10 | 16 | 17
| G04 | Electric energy storage | C406.3.5 | 16 | 16 | 18 | 17 | 19 | 21 | 21 | 23 | 26 | 22 | 24 | 24 | 23 | 24 | 24 | 20 | 22 | 19 | 19
| G05 | Cooling energy storage | C406.3.6 | 36 | 9 | 46 | 21 | 36 | 32 | 39 | 62 | 39 | 24 | 37 | 22 | 20 | 28 | 13 | 16 | 31 | 3 | 4
| G06 | SHW energy storage | C406.3.7 | 5 | 5 | 6 | 5 | 6 | 6 | 7 | 7 | 8 | 7 | 7 | 8 | 7 | 7 | 8 | 7 | 7 | 7 | 6
| G07 | Building thermal mass | C406.3.8 | 7 | 2 | 11 | 5 | 17 | 28 | 23 | 27 | 63 | 21 | 44 | 48 | 37 | 60 | 38 | 31 | 50 | 47 | 21
BASE ENERGY CREDITS FOR GROUP S-1 AND S-2 OCCUPANCIES
| Warehouse |  |  | Climate Zone
| ID | Energy Credit Measure | Section | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
| E01 | Envelope Performance | C406.2.1.1 | Determined in accordance with Section C406.2.1.1
| E02 | UA reduction (15%) | C406.2.1.2 | 14 | 14 | 1 | 12 | 1 | 9 | 27 | 16 | 2 | 37 | 29 | 39 | 44 | 47 | 50 | 43 | 52 | 55 | 74
| E03 | Envelope leakage reduction | C406.2.1.3 | 2 | 2 | 1 | 2 | 1 | 3 | 31 | 3 | 1 | 77 | 14 | 17 | 92 | 25 | 8 | 95 | 71 | 69 | 26
| E04 | Add Roof Insulation | C406.2.1.4 | 13 | 12 | 10 | 11 | 10 | 11 | 18 | 17 | 7 | 14 | 19 | 18 | 14 | 20 | 22 | 10 | 14 | 12 | 19
| E05 | Add Wall Insulation | C406.2.1.5 | 19 | 23 | 13 | 21 | 7 | 10 | 15 | 12 | 3 | 10 | 12 | 13 | 9 | 12 | 12 | 7 | 9 | 9 | 8
| E06 | Improve Fenestration | C406.2.1.6 | 7 | 5 | 8 | 7 | 6 | 6 | 2 | 4 | 2 | 4 | 1 | 6 | 5 | 1 | 7 | 3 | 4 | 4 | 7
| H01 | HVAC Performance | C406.2.2.1 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| H02 | Heating efficiency | C406.2.2.2 | x | x | x | x | x | x | 16 | 3 | 1 | 33 | 17 | 22 | 41 | 31 | 21 | 44 | 38 | 43 | 43
| H03 | Cooling efficiency | C406.2.2.3 | 7 | 7 | 4 | 5 | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | x | x | x | x
| H04 | Residential HVAC control | C406.2.2.4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| H05 | DOAS/fan control | C406.2.2.5 | 35 | 37 | 26 | 33 | 24 | 27 | 77 | 35 | 14 | 141 | 83 | 96 | 168 | 132 | 90 | 180 | 157 | 177 | 178
| W01 | SHW preheat recovery | C406.2.3.1 | 8 | 7 | 9 | 8 | 10 | 10 | 8 | 10 | 12 | 5 | 8 | 8 | 4 | 6 | 9 | 3 | 4 | 3 | 3
| W02 | Heat pump water heater | C406.2.3.1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 1 | 2 | 2 | 1 | 2 | 2 | 1 | 1 | 1 | 1
| W03 | Efficient gas water heater | C406.2.3.1 | 4 | 4 | 5 | 4 | 5 | 5 | 4 | 5 | 6 | 3 | 4 | 4 | 2 | 3 | 5 | 2 | 2 | 2 | 2
| W04 | SHW pipe insulation | C406.2.3.2 | 3 | 3 | 4 | 3 | 3 | 3 | 2 | 3 | 4 | 2 | 2 | 3 | 1 | 2 | 3 | 1 | 1 | 1 | 1
| W05 | Point of use water heaters | C406.2.3.3 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| W06 | Thermostatic bal. valves | C406.2.3.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
| W07 | SHW heat trace system | C406.2.3.3 | 4 | 4 | 4 | 3 | 4 | 4 | 3 | 4 | 5 | 2 | 3 | 3 | 2 | 2 | 4 | 2 | 2 | 2 | 2
| W08 | SHW submeters | C406.2.3.4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| W09 | SHW flow reduction | C406.2.3.5 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| W10 | Shower heat recovery | C406.2.3.6 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| P01 | Energy monitoring | C406.2.4 | 5 | 5 | 6 | 6 | 6 | 6 | 5 | 6 | 6 | 5 | 5 | 5 | 5 | 5 | 6 | 5 | 5 | 5 | 5
| L01 | Lighting Performance | C406.2.5.1 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| L02 | Lighting dimming & tuning | C406.2.5.2 | 10 | 10 | 12 | 11 | 12 | 14 | 9 | 12 | 14 | 6 | 9 | 9 | 3 | 6 | 9 | 3 | 5 | 3 | 2
| L03 | Increase occp. sensor | C406.2.5.3 | 12 | 12 | 14 | 13 | 15 | 14 | 12 | 14 | 17 | 7 | 11 | 11 | 5 | 7 | 11 | 4 | 6 | 3 | 3
| L04 | Increase daylight area | C406.2.5.4 | 15 | 14 | 18 | 16 | 18 | 17 | 13 | 16 | 21 | 7 | 12 | 11 | 5 | 8 | 10 | 4 | 6 | 6 | 5
| L05 | Residential light control | C406.2.5.5 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| L06 | Light power reduction | C406.2.5.7 | 14 | 14 | 17 | 16 | 17 | 17 | 13 | 17 | 19 | 8 | 13 | 12 | 5 | 8 | 12 | 4 | 6 | 4 | 2
| Q01 | Efficient elevator | C406.2.7.1 | 15 | 14 | 18 | 16 | 18 | 18 | 15 | 18 | 21 | 9 | 14 | 14 | 7 | 10 | 14 | 5 | 7 | 5 | 5
| Q02 | Commercial kitchen equip. | C406.2.7.2 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| Q03 | Residential kitchen equip. | C406.2.7.3 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| Q04 | Fault detection | C406.2.7.4 | 3 | 3 | 2 | 3 | 2 | 2 | 3 | 2 | 1 | 5 | 3 | 3 | 5 | 4 | 3 | 6 | 5 | 6 | 6
| RENEWABLE AND LOAD MANAGEMENT CREDITS FOR GROUP S-1 AND S-2 OCCUPANCIES | [20 empty] | Warehouse
| ID | Energy Credit Abbreviated Title | Section | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
| R01 | Renewable Energy | C406.3.1 | 38 | 37 | 55 | 45 | 53 | 53 | 49 | 58 | 66 | 36 | 56 | 38 | 29 | 41 | 36 | 24 | 32 | 23 | 16
| G01 | Lighting load management | C406.3.2 | 13 | 26 | 32 | 28 | 32 | 35 | 36 | 33 | 36 | 31 | 27 | 37 | 32 | 23 | 28 | 36 | 22 | 25 | 22
| G02 | HVAC load management | C406.3.3 | 18 | 46 | 37 | 37 | 28 | 36 | 29 | 26 | 22 | 23 | 17 | 12 | 16 | 13 | 5 | 14 | 8 | 10 | 3
| G03 | Automated shading | C406.3.4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| G04 | Electric energy storage | C406.3.5 | 40 | 40 | 47 | 41 | 47 | 44 | 40 | 44 | 42 | 30 | 38 | 31 | 21 | 31 | 26 | 24 | 29 | 23 | 21
| G05 | Cooling energy storage | C406.3.6 | 20 | 5 | 21 | 11 | 14 | 14 | 11 | 21 | 5 | 5 | 9 | 2 | 2 | 5 | 1 | 1 | 3 | x | x
| G06 | SHW energy storage | C406.3.7 | 3 | 3 | 3 | 3 | 4 | 3 | 4 | 4 | 4 | 3 | 4 | 4 | 3 | 3 | 4 | 2 | 2 | 2 | 2
| G07 | Building thermal mass | C406.3.8 | 7 | 2 | 12 | 5 | 17 | 29 | 23 | 28 | 66 | 18 | 44 | 47 | 28 | 56 | 37 | 20 | 39 | 29 | 13
BASE ENERGY CREDITS FOR OTHER OCCUPANCIESa
| Other |  |  | Climate Zone
| ID | Energy Credit Measure | Section | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
| E01 | Envelope Performance | C406.2.1.1 | Determined in accordance with Section C406.2.1.1
| E02 | UA reduction (15%) | C406.2.1.2 | 7 | 8 | 3 | 7 | 5 | 5 | 11 | 7 | 2 | 18 | 10 | 14 | 26 | 20 | 19 | 24 | 25 | 29 | 32
| E03 | Envelope leakage reduction | C406.2.1.3 | 6 | 4 | 5 | 4 | 3 | 7 | 12 | 3 | 2 | 28 | 5 | 6 | 36 | 9 | 3 | 41 | 27 | 33 | 15
| E04 | Add Roof Insulation | C406.2.1.4 | 4 | 4 | 3 | 4 | 4 | 4 | 8 | 6 | 2 | 7 | 6 | 7 | 9 | 8 | 9 | 9 | 10 | 9 | 12
| E05 | Add Wall Insulation | C406.2.1.5 | 16 | 19 | 11 | 17 | 5 | 6 | 10 | 7 | 2 | 9 | 6 | 8 | 9 | 7 | 7 | 9 | 9 | 10 | 8
| E06 | Improve Fenestration | C406.2.1.6 | 4 | 4 | 3 | 4 | 5 | 6 | 6 | 4 | 1 | 9 | 4 | 7 | 11 | 7 | 6 | 16 | 14 | 8 | 8
| H01 | HVAC Performance | C406.2.2.1 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| H02 | Heating efficiency | C406.2.2.2 | x | x | x | x | x | x | 6 | 2 | 3 | 11 | 6 | 8 | 15 | 11 | 9 | 18 | 15 | 19 | 23
| H03 | Cooling efficiency | C406.2.2.3 | 7 | 7 | 5 | 5 | 4 | 3 | 1 | 2 | 1 | x | x | x | x | x | x | x | x | x | x
| H04 | Residential HVAC control | C406.2.2.4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| H05 | DOAS/fan control | C406.2.2.5 | 37 | 36 | 31 | 34 | 30 | 28 | 43 | 32 | 23 | 61 | 42 | 49 | 75 | 61 | 49 | 90 | 77 | 93 | 90
| W01 | SHW preheat recovery | C406.2.3.1 | 18 | 19 | 22 | 21 | 25 | 26 | 28 | 29 | 34 | 29 | 31 | 34 | 29 | 31 | 35 | 26 | 29 | 27 | 26
| W02 | Heat pump water heater | C406.2.3.1 | 12 | 12 | 15 | 14 | 17 | 17 | 20 | 20 | 24 | 21 | 22 | 25 | 21 | 23 | 26 | 20 | 22 | 21 | 20
| W03 | Efficient gas water heater | C406.2.3.1 | 11 | 11 | 13 | 13 | 15 | 16 | 17 | 17 | 21 | 18 | 19 | 21 | 18 | 19 | 22 | 16 | 18 | 17 | 16
| W04 | SHW pipe insulation | C406.2.3.2 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 4 | 4 | 5 | 4 | 4 | 5 | 3 | 4 | 3 | 3
| W05 | Point of use water heaters | C406.2.3.3 | 8 | 10 | 11 | 10 | 11 | 12 | 12 | 12 | 14 | 13 | 13 | 14 | 13 | 13 | 14 | 11 | 12 | 12 | 11
| W06 | Thermostatic bal. valves | C406.2.3.3 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 2 | 1 | 1 | 1 | 1
| W07 | SHW heat trace system | C406.2.3.3 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 7 | 6 | 6 | 7 | 5 | 6 | 7 | 5 | 5 | 5 | 5
| W08 | SHW submeters | C406.2.3.4 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| W09 | SHW flow reduction | C406.2.3.5 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| W10 | Shower heat recovery | C406.2.3.6 | 6 | 6 | 7 | 7 | 8 | 9 | 10 | 10 | 11 | 10 | 11 | 12 | 10 | 11 | 12 | 10 | 11 | 10 | 10
| P01 | Energy monitoring | C406.2.4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4
| L01 | Lighting Performance | C406.2.5.1 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| L02 | Lighting dimming & tuning | C406.2.5.2 | 5 | 5 | 5 | 5 | 6 | 6 | 5 | 6 | 7 | 5 | 5 | 5 | 4 | 4 | 5 | 3 | 4 | 3 | 2
| L03 | Increase occp. sensor | C406.2.5.3 | 5 | 6 | 6 | 6 | 7 | 7 | 6 | 7 | 8 | 5 | 6 | 6 | 4 | 5 | 6 | 3 | 4 | 3 | 2
| L04 | Increase daylight area | C406.2.5.4 | 7 | 8 | 9 | 8 | 9 | 9 | 8 | 8 | 10 | 6 | 7 | 7 | 5 | 6 | 6 | 4 | 5 | 5 | 4
| L05 | Residential light control | C406.2.5.5 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| L06 | Light power reduction | C406.2.5.7 | 7 | 7 | 8 | 7 | 8 | 8 | 7 | 8 | 9 | 5 | 7 | 6 | 4 | 5 | 6 | 4 | 4 | 3 | 2
| Q01 | Efficient elevator | C406.2.7.1 | 4 | 4 | 5 | 4 | 5 | 5 | 5 | 5 | 6 | 4 | 5 | 5 | 4 | 4 | 5 | 3 | 4 | 3 | 3
| Q02 | Commercial kitchen equip. | C406.2.7.2 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| Q03 | Residential kitchen equip. | C406.2.7.3 | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x | x
| Q04 | Fault detection | C406.2.7.4 | 3 | 3 | 3 | 3 | 3 | 2 | 3 | 2 | 2 | 3 | 3 | 2 | 3 | 3 | 2 | 4 | 3 | 4 | 4
| RENEWABLE AND LOAD MANAGEMENT CREDITS FOR OTHER OCCUPANCIES | [20 empty] | Other
| ID | Energy Credit Abbreviated Title | Section | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
| R01 | Renewable Energy | C406.3.1 | 12 | 13 | 16 | 14 | 16 | 18 | 17 | 20 | 21 | 13 | 18 | 13 | 12 | 15 | 14 | 11 | 13 | 10 | 8
| G01 | Lighting load management | C406.3.2 | 11 | 13 | 14 | 14 | 14 | 16 | 15 | 16 | 14 | 14 | 16 | 16 | 13 | 14 | 16 | 14 | 13 | 12 | 12
| G02 | HVAC load management | C406.3.3 | 24 | 24 | 23 | 22 | 20 | 23 | 21 | 21 | 18 | 18 | 20 | 17 | 16 | 18 | 14 | 13 | 14 | 13 | 6
| G03 | Automated shading | C406.3.4 | 5 | 6 | 7 | 9 | 8 | 9 | 7 | 9 | 8 | 5 | 9 | 7 | 5 | 8 | 7 | 5 | 6 | 6 | 9
| G04 | Electric energy storage | C406.3.5 | 14 | 15 | 16 | 15 | 16 | 17 | 17 | 18 | 19 | 16 | 17 | 17 | 15 | 16 | 17 | 14 | 15 | 14 | 14
| G05 | Cooling energy storage | C406.3.6 | 28 | 7 | 34 | 15 | 25 | 22 | 25 | 39 | 20 | 14 | 22 | 12 | 11 | 17 | 7 | 9 | 18 | 2 | 3
| G06 | SHW energy storage | C406.3.7 | 9 | 9 | 11 | 10 | 11 | 11 | 11 | 12 | 13 | 11 | 12 | 13 | 11 | 11 | 12 | 10 | 11 | 10 | 9
| G07 | Building thermal mass | C406.3.8 | 6 | 2 | 9 | 4 | 13 | 21 | 16 | 20 | 44 | 14 | 31 | 33 | 24 | 42 | 25 | 20 | 33 | 29 | 13
Available load management credits include G01, G02, G03, G06
G04: batteries, G05: cooling storage, & G07: thermal mass are excluded
Available efficiency credit multipliers found at cells Y114:Y156

## Carry-overCurrentPC
Carryover analysis for base code proposal
Alternate reasonable measure selections without improvements above minimum regulated equipment efficiency
| Selections w/o improved equip. efficiency |  | R-2/4, I-1 | I-2 | R-1 | B | A-2 | M | E | S-1/2
| ID | Measure | MF | Health | Hotel | Office | Rest | Retail | School | Whse | Other
| E03 | Envelope Leakage Reduction | Y | Y | Y | Y | Y | Y | Y | Y | Y
| E04 | Add R-5 Roof Insulation | Y | Y | Y | Y | Y | Y | Y | Y | Y | R-10 in CZ 8
| E05 | Add R-2.5 ci Wall Insulation | Y | Y | Y | Y | Y | Y | Y | Y | Y | R-5 in CZ 8
| E06 | Improve Fenestration | Y | Y | Y | Y | Y | Y | Y | Y | Y
| H04 | Residential HVAC control. | Y
| W01 | SHW preheat recovery |  | 30% | [7 empty] | of SHW load
| W02 | Heat pump water heater |  |  | 30% |  | 30% |  |  |  |  | of SHW load
| W04 | SHW pipe insulation |  |  |  |  | Y | Y | Y |  | Y
| W05 | Point of use water heaters |  |  |  | Y |  |  | Y
| W06 | Thermostatic balancing valves | N | [10 empty] | << removed to allow individual apartment water heaters
| W07 | SHW heat trace system |  | Y | Y
| W09 | SHW flow reduction | Y |  | Y
| L04 | Increase daylight area |  |  |  | 5% |  | 10% |  | 5% |  | of floor area |  | << reduced to match a more broad array of building configurations
| L05 | Residential light control | Y
| L06 | Lighting power reduction | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | of LPD
| Q01 | Efficient Elevator |  | Y | Y | Y | N | [6 empty] | << removed as elevators less likely in restaurants
| Q02 | Efficient Commercial Kitchen Equipment |  |  |  |  | Y
| Q04 | Fault detection |  | Y | Y | Y | Y | Y | Y | Y | Y
Energy Efficiency Credits Achieved by reasonable package without equipment efficiency improvement
| Use group and building type |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
| R-2, R-4, I-1 | Multi-family/Dormitory | 71.5 | 66.5 | 68.5 | 80.5 | 82 | 103.5 | 97 | 79.5 | 96 | 120.5 | 93 | 97 | 130.5 | 121 | 95.5 | 144.5 | 140.5 | 124.5 | 138
| I-2 | Healthcare | 29.5 | 30 | 29 | 31 | 32.5 | 36.5 | 39 | 32.5 | 33.5 | 39.5 | 33 | 36 | 39.5 | 30.5 | 28 | 38.5 | 35 | 42.5 | 30
| R-1 | Hotel/Motel | 58.5 | 59.5 | 60 | 63.5 | 53.5 | 68.5 | 66.5 | 62 | 66.5 | 80 | 65.5 | 70 | 91.5 | 72.5 | 74 | 102.5 | 87 | 96 | 87
| B | Office Buildings | 57.5 | 59 | 61 | 60.5 | 62 | 61 | 68 | 56 | 56.5 | 67 | 53.5 | 61 | 72.5 | 59 | 53.5 | 86 | 76 | 78 | 64
| A-2 | Restaurant Buildings | 54 | 56 | 60 | 59 | 64 | 68.5 | 78.5 | 71 | 73 | 87.5 | 72 | 76.5 | 96 | 76 | 73.5 | 101 | 93 | 88.5 | 68
| M | Retail Buildings | 99 | 98.5 | 97.5 | 103.5 | 86 | 91 | 106.5 | 94 | 91 | 120 | 89.5 | 93.5 | 124 | 93 | 81 | 134.5 | 121 | 111 | 103
| E | Education Buildings | 45.5 | 46.5 | 39 | 44.5 | 43 | 45.5 | 55 | 44.5 | 36 | 54 | 42 | 51 | 59.5 | 54 | 59.5 | 73 | 69.5 | 56.5 | 73
| S-1, S-2 | Warehouse | 71 | 69.5 | 74.5 | 76 | 69.5 | 72.5 | 91.5 | 73.5 | 67 | 121 | 70.5 | 76.5 | 128.5 | 70 | 69 | 124.5 | 109.5 | 103.5 | 75
| Other | Other | 41 | 39.5 | 38 | 39.5 | 35.5 | 40 | 48 | 35.5 | 30 | 59 | 36 | 39.5 | 66 | 41.5 | 36.5 | 76 | 64.5 | 61.5 | 56
Requirements with PNNL PCs
Min of
5 |  | Building Use Type | Climate Zone
% of Req'd |  |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
6.165% | R-2, R-4, I-1 | Multi-family/Dormitory | 65 | 66 | 67 | 77 | 80 | 86 | 80 | 81 | 90 | 86 | 90 | 90 | 86 | 90 | 90 | 70 | 89 | 80 | 78
12.48% | I-2 | Healthcare | 43 | 42 | 38 | 37 | 36 | 38 | 32 | 32 | 30 | 36 | 36 | 35 | 43 | 43 | 44 | 46 | 47 | 50 | 53
6.363% | R-1 | Hotel/Motel | 63 | 62 | 66 | 65 | 70 | 71 | 77 | 80 | 84 | 81 | 83 | 88 | 85 | 86 | 90 | 83 | 87 | 87 | 85
7.263% | B | Office Buildings | 62 | 62 | 64 | 66 | 66 | 65 | 64 | 64 | 68 | 70 | 72 | 74 | 71 | 73 | 77 | 71 | 74 | 74 | 71
7.132% | A-2 | Restaurant Buildings | 70 | 70 | 72 | 72 | 75 | 75 | 70 | 73 | 82 | 69 | 74 | 78 | 67 | 72 | 78 | 60 | 67 | 57 | 51
6.83% | M | Retail Buildings | 80 | 79 | 83 | 79 | 81 | 84 | 67 | 74 | 87 | 80 | 66 | 65 | 79 | 62 | 50 | 75 | 67 | 75 | 58
8.183% | E | School/Education Buildings | 56 | 57 | 55 | 58 | 58 | 57 | 59 | 62 | 59 | 61 | 66 | 62 | 64 | 67 | 67 | 65 | 67 | 63 | 58
7.047% | S-1, S-2 | Warehouse and Semiheated | 61 | 60 | 61 | 60 | 58 | 57 | 44 | 54 | 62 | 85 | 68 | 75 | 90 | 82 | 72 | 90 | 89 | 90 | 90
14.73% | Other | Other | 31 | 31 | 31 | 32 | 32 | 33 | 30 | 32 | 36 | 35 | 35 | 35 | 37 | 36 | 36 | 36 | 37 | 36 | 34
8.466%
Carryover surplus load management points needed with no increases in regulated equipment efficiency
| Use group and building type |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
| R-2, R-4, I-1 | Multi-family/Dormitory | -7 | -1 | -2 | -4 | -2 | -18 | -17 | 2 | -6 | -35 | -3 | -7 | -45 | -31 | -6 | -75 | -52 | -45 | -60
| I-2 | Healthcare | 14 | 12 | 9 | 6 | 4 | 2 | -7 | -1 | -4 | -4 | 3 | -1 | 4 | 13 | 16 | 8 | 12 | 8 | 23
| R-1 | Hotel/Motel | 5 | 3 | 6 | 2 | 17 | 3 | 11 | 18 | 18 | 1 | 18 | 18 | -7 | 14 | 16 | -20 | 0 | -9 | -2
| B | Office Buildings | 5 | 3 | 3 | 6 | 4 | 4 | -4 | 8 | 12 | 3 | 19 | 13 | -2 | 14 | 24 | -15 | -2 | -4 | 7
| A-2 | Restaurant Buildings | 16 | 14 | 12 | 13 | 11 | 7 | -9 | 2 | 9 | -19 | 2 | 2 | -29 | -4 | 5 | -41 | -26 | -32 | -17
| M | Retail Buildings | -19 | -20 | -15 | -25 | -5 | -7 | -40 | -20 | -4 | -40 | -24 | -29 | -45 | -31 | -31 | -60 | -54 | -36 | -45
| E | Education Buildings | 11 | 11 | 16 | 14 | 15 | 12 | 4 | 18 | 23 | 7 | 24 | 11 | 5 | 13 | 8 | -8 | -3 | 7 | -15
| S-1, S-2 | Warehouse | -10 | -10 | -14 | -16 | -12 | -16 | -48 | -20 | -5 | -36 | -3 | -2 | -39 | 12 | 3 | -35 | -21 | -14 | 15
| Other | Other | -10 | -9 | -7 | -8 | -4 | -7 | -18 | -4 | 6 | -24 | -1 | -5 | -29 | -6 | -1 | -40 | -28 | -26 | -22
|  | Minimum Carryover Credit | 5 |  |  |  | Roundoff Carryover Credit adder | 2
| Carryover surplus load management points allowed | [5 empty] | Table C406.1.1(2)
% of Req'd | Use group and building type |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
6.165% | R-2, R-4, I-1 | Multi-family/Dormitory | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
24.7% | I-2 | Healthcare | 16 | 14 | 11 | 8 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 15 | 18 | 10 | 14 | 10 | 25
13.8% | R-1 | Hotel/Motel | 7 | 5 | 8 | 5 | 19 | 5 | 13 | 20 | 20 | 5 | 20 | 20 | 5 | 16 | 18 | 5 | 5 | 5 | 5
13.61% | B | Office Buildings | 7 | 5 | 5 | 8 | 6 | 6 | 5 | 10 | 14 | 5 | 21 | 15 | 5 | 16 | 26 | 5 | 5 | 5 | 9
11.86% | A-2 | Restaurant Buildings | 18 | 16 | 14 | 15 | 13 | 9 | 5 | 5 | 11 | 5 | 5 | 5 | 5 | 5 | 7 | 5 | 5 | 5 | 5
6.83% | M | Retail Buildings | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
21.19% | E | Education Buildings | 13 | 13 | 18 | 16 | 17 | 14 | 6 | 20 | 25 | 9 | 26 | 13 | 7 | 15 | 10 | 5 | 5 | 9 | 5
8.605% | S-1, S-2 | Warehouse | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 14 | 5 | 5 | 5 | 5 | 17
15.19% | Other | Other | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
13.55%
4.472% | 33% | of recent new construction has fossil fuels, so impact on energy credits is | [21 empty] | PV Credits for 0.1 W/sf
0.4025% | 9% | Maximum energy credits showing small % of total building energy use
PV W/sf required to meet carry-over need with no LM carry over
| Use group and building type |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8 |  |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
| R-2, R-4, I-1 | Multi-family/Dormitory | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0095238 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5 | Multi-family/Dormitory | 9 | 15 | 11 | 17 | 18 | 20 | 19 | 21 | 13 | 10 | 13 | 9 | 9 | 11 | 10 | 9 | 10 | 9 | 7
| I-2 | Healthcare | 0.23333 | 0.2 | 0.15 | 0.1 | 0.066667 | 0.025 | 0 | 0 | 0 | 0 | 0.0375 | 0 | 0.066667 | 0.18571 | 0.22857 | 0.13333 | 0.17143 | 0.16 | 0.575 |  | Healthcare | 6 | 6 | 6 | 6 | 6 | 8 | 7 | 9 | 8 | 6 | 8 | 6 | 6 | 7 | 7 | 6 | 7 | 5 | 4
| R-1 | Hotel/Motel | 0.055556 | 0.0375 | 0.05 | 0.022222 | 0.15455 | 0.027273 | 0.11 | 0.15 | 0.13846 | 0.011111 | 0.15 | 0.225 | 0 | 0.12727 | 0.17778 | 0 | 0 | 0 | 0 |  | Hotel/Motel | 9 | 8 | 12 | 9 | 11 | 11 | 10 | 12 | 13 | 9 | 12 | 8 | 9 | 11 | 9 | 8 | 9 | 7 | 5
| B | Office Buildings | 0.035714 | 0.021429 | 0.017647 | 0.04 | 0.023529 | 0.021053 | 0 | 0.036364 | 0.05 | 0.017647 | 0.086364 | 0.08125 | 0 | 0.077778 | 0.13333 | 0 | 0 | 0 | 0.063636 |  | Office | 14 | 14 | 17 | 15 | 17 | 19 | 18 | 22 | 24 | 17 | 22 | 16 | 14 | 18 | 18 | 14 | 17 | 14 | 11
| A-2 | Restaurant Buildings | 0.8 | 0.7 | 0.6 | 0.65 | 0.55 | 0.35 | 0 | 0.066667 | 0.225 | 0 | 0.066667 | 0.1 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0 |  | Restaurant | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 4 | 2 | 3 | 2 | 2 | 3 | 2 | 2 | 2 | 2 | 1
| M | Retail Buildings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Retail | 8 | 8 | 12 | 9 | 11 | 12 | 12 | 17 | 17 | 11 | 13 | 9 | 10 | 11 | 10 | 9 | 10 | 9 | 6
| E | Education Buildings | 0.11 | 0.1 | 0.12308 | 0.11667 | 0.11538 | 0.075 | 0.026667 | 0.085714 | 0.10455 | 0.046667 | 0.12632 | 0.073333 | 0.035714 | 0.076471 | 0.05 | 0 | 0 | 0.058333 | 0 |  | School/Education | 10 | 11 | 13 | 12 | 13 | 16 | 15 | 21 | 22 | 15 | 19 | 15 | 14 | 17 | 16 | 13 | 16 | 12 | 10
| S-1, S-2 | Warehouse | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.029268 | 0.0083333 | 0 | 0 | 0 | 0.09375 |  | Warehouse | 38 | 37 | 55 | 45 | 53 | 53 | 49 | 58 | 66 | 36 | 56 | 38 | 29 | 41 | 36 | 24 | 32 | 23 | 16
Load Management Points available for carryover net of revised (lowered) requirement (CED1-188)
Surplus LM (G01,G02,G06) after meet LM/PV requirements with only LM
| Building Occupancy Group |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | SA | SB | SC | 6A | 6B | 7 | 8
| R-2, R-4, and 1-1 | Multi-family/Dormitory | 41 | 28 | 18 | 19 | 6 | 16 | 12 | 6 | 24 | 16 | 26 | 27 | 21 | 19 | 23 | 10 | 12 | 15 | 20
| I-2 | Healthcare | 2 | 3 | 2 | 2 | 0 | 9 | 0 | -4 | 1 | 3 | 6 | 4 | 4 | 4 | 3 | 4 | 1 | 3 | 3
| R-1 | Hotel/Motel | 7 | 9 | 4 | 8 | 6 | 7 | 9 | 6 | 5 | 11 | 6 | 15 | 10 | 7 | 13 | 10 | 10 | 11 | 14
| B | Office Buildings | -23 | -13 | -18 | -15 | -19 | -29 | -21 | -25 | -33 | -15 | -29 | -14 | -12 | -19 | -16 | -14 | -18 | -12 | -14
| A-2 | Restaurant Buildings | 41 | 35 | 48 | 38 | 42 | 38 | 39 | 33 | 34 | 32 | 28 | 29 | 31 | 25 | 24 | 27 | 26 | 24 | 12
| M | Retail Buildings | -13 | -13 | -4 | 0 | -3 | -14 | -5 | -9 | -16 | 5 | -7 | 10 | 1 | 1 | 11 | 0 | 1 | 4 | -6
| E | Education Buildings | 3 | 5 | 12 | 4 | 5 | 5 | 3 | -9 | -16 | 0 | 0 | 2 | -1 | 4 | -12 | -1 | 2 | -1 | -5
| S-1 and S-2 | Warehouse | -55 | -15 | -18 | -22 | -26 | -16 | -21 | -27 | -28 | -33 | -42 | -37 | -39 | -51 | -53 | -32 | -54 | -34 | -27
| All Other |  | 9 | 7 | 2 | 4 | -1 | -2 | -2 | -7 | -11 | 3 | -4 | 4 | 3 | -1 | -2 | 1 | -1 | 3 | -1
Restaurant Building example
|  | Carryover Needed | 18 | 16 | 14 | 15 | 13 | 9 | 5 | 5 | 11 | 5 | 5 | 5 | 5 | 5 | 7 | 5 | 5 | 5 | 5
|  | Surplus LM Points (No PV) | 41 | 35 | 48 | 38 | 42 | 38 | 39 | 33 | 34 | 32 | 28 | 29 | 31 | 25 | 24 | 27 | 26 | 24 | 12
| 0.15 | LM Credits applyable | 6.15 | 5.25 | 7.2 | 5.7 | 6.3 | 5.7 | 5 | 4.95 | 5.1 | 4.8 | 4.2 | 4.35 | 4.65 | 3.75 | 3.6 | 4.05 | 3.9 | 3.6 | 1.8
| 0.3 |  | 12.3 | 10.5 | 14 | 11.4 | 12.6 | 9 | 5 | 5 | 10.2 | 5 | 5 | 5 | 5 | 5 | 7 | 5 | 5 | 5 | 3.6
| 0.5 |  | 18 | 16 | 14 | 15 | 13 | 9 | 5 | 5 | 11 | 5 | 5 | 5 | 5 | 5 | 7 | 5 | 5 | 5 | 5
| 0.7 | Agreed to adjustment | 18 | 16 | 14 | 15 | 13 | 9 | 5 | 5 | 11 | 5 | 5 | 5 | 5 | 5 | 7 | 5 | 5 | 5 | 5
| 1 |  | 18 | 16 | 14 | 15 | 13 | 9 | 5 | 5 | 11 | 5 | 5 | 5 | 5 | 5 | 7 | 5 | 5 | 5 | 5
|  |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
|  | Renewable Credits per 0.1 W/sf | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 4 | 2 | 3 | 2 | 2 | 3 | 2 | 2 | 2 | 2 | 1
| 0.15 | Renewable needed W/sf | 0.5925 | 0.5375 | 0.34 | 0.465 | 0.335 | 0.165 | 0 | 0.0016667 | 0.1475 | 0.01 | 0.026667 | 0.0325 | 0.0175 | 0.041667 | 0.17 | 0.0475 | 0.055 | 0.07 | 0.32 | 1.5
| 0.3 |  | 0.285 | 0.275 | 0 | 0.18 | 0.02 | 0 | 0 | 0 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14
| 0.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.7 | Agreed to adjustment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Health building example
|  | Carryover Needed | 16 | 14 | 11 | 8 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 15 | 18 | 10 | 14 | 10 | 25
|  | Surplus LM Points (No PV) | 2 | 3 | 2 | 2 | 0 | 9 | 0 | -4 | 1 | 3 | 6 | 4 | 4 | 4 | 3 | 4 | 1 | 3 | 3
| 0.15 | LM Credits applyable | 0.3 | 0.45 | 0.3 | 0.3 | 0 | 1.35 | 0 | 0 | 0.15 | 0.45 | 0.9 | 0.6 | 0.6 | 0.6 | 0.45 | 0.6 | 0.15 | 0.45 | 0.45
| 0.3 |  | 0.6 | 0.9 | 0.6 | 0.6 | 0 | 2.7 | 0 | 0 | 0.3 | 0.9 | 1.8 | 1.2 | 1.2 | 1.2 | 0.9 | 1.2 | 0.3 | 0.9 | 0.9
| 0.5 |  | 1 | 1.5 | 1 | 1 | 0 | 4.5 | 0 | 0 | 0.5 | 1.5 | 3 | 2 | 2 | 2 | 1.5 | 2 | 0.5 | 1.5 | 1.5
| 0.7 | Agreed to adjustment | 1.4 | 2.1 | 1.4 | 1.4 | 0 | 5 | 0 | 0 | 0.7 | 2.1 | 4.2 | 2.8 | 2.8 | 2.8 | 2.1 | 2.8 | 0.7 | 2.1 | 2.1
| 1 |  | 2 | 3 | 2 | 2 | 0 | 5 | 0 | 0 | 1 | 3 | 5 | 4 | 4 | 4 | 3 | 4 | 1 | 3 | 3
|  |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
|  | Renewable Credits per 0.1 W/sf | 6 | 6 | 6 | 6 | 6 | 8 | 7 | 9 | 8 | 6 | 8 | 6 | 6 | 7 | 7 | 6 | 7 | 5 | 4
| 0.15 | Renewable needed W/sf | 0.26167 | 0.22583 | 0.17833 | 0.12833 | 0.1 | 0.045625 | 0.071429 | 0.055556 | 0.060625 | 0.075833 | 0.05125 | 0.073333 | 0.09 | 0.20571 | 0.25071 | 0.15667 | 0.19786 | 0.191 | 0.61375 | 1.5
| 0.3 |  | 0.25667 | 0.21833 | 0.17333 | 0.12333 | 0.1 | 0.02875 | 0.071429 | 0.055556 | 0.05875 | 0.068333 | 0.04 | 0.063333 | 0.08 | 0.19714 | 0.24429 | 0.14667 | 0.19571 | 0.182 | 0.6025
| 0.5 |  | 0.25 | 0.20833 | 0.16667 | 0.11667 | 0.1 | 0.00625 | 0.071429 | 0.055556 | 0.05625 | 0.058333 | 0.025 | 0.05 | 0.066667 | 0.18571 | 0.23571 | 0.13333 | 0.19286 | 0.17 | 0.5875
| 0.7 | Agreed to adjustment | 0.24333 | 0.19833 | 0.16 | 0.11 | 0.1 | 0 | 0.071429 | 0.055556 | 0.05375 | 0.048333 | 0.01 | 0.036667 | 0.053333 | 0.17429 | 0.22714 | 0.12 | 0.19 | 0.158 | 0.5725
| 1 |  | 0.23333 | 0.18333 | 0.15 | 0.1 | 0.1 | 0 | 0.071429 | 0.055556 | 0.05 | 0.033333 | 0 | 0.016667 | 0.033333 | 0.15714 | 0.21429 | 0.1 | 0.18571 | 0.14 | 0.55
Education Building example
|  | Carryover Needed | 13 | 13 | 18 | 16 | 17 | 14 | 6 | 20 | 25 | 9 | 26 | 13 | 7 | 15 | 10 | 5 | 5 | 9 | 5
|  | Surplus LM Points (No PV) | 3 | 5 | 12 | 4 | 5 | 5 | 3 | -9 | -16 | 0 | 0 | 2 | -1 | 4 | -12 | -1 | 2 | -1 | -5
| 0.15 | LM Credits applyable | 0.45 | 0.75 | 1.8 | 0.6 | 0.75 | 0.75 | 0.45 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0.6 | 0 | 0 | 0.3 | 0 | 0
| 0.3 |  | 0.9 | 1.5 | 3.6 | 1.2 | 1.5 | 1.5 | 0.9 | 0 | 0 | 0 | 0 | 0.6 | 0 | 1.2 | 0 | 0 | 0.6 | 0 | 0
| 0.5 |  | 1.5 | 2.5 | 6 | 2 | 2.5 | 2.5 | 1.5 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 0 | 1 | 0 | 0
| 0.7 | Agreed to adjustment | 2.1 | 3.5 | 8.4 | 2.8 | 3.5 | 3.5 | 2.1 | 0 | 0 | 0 | 0 | 1.4 | 0 | 2.8 | 0 | 0 | 1.4 | 0 | 0
| 1 |  | 3 | 5 | 12 | 4 | 5 | 5 | 3 | 0 | 0 | 0 | 0 | 2 | 0 | 4 | 0 | 0 | 2 | 0 | 0
|  |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
|  | Renewable Credits per 0.1 W/sf | 10 | 11 | 13 | 12 | 13 | 16 | 15 | 21 | 22 | 15 | 19 | 15 | 14 | 17 | 16 | 13 | 16 | 12 | 10
| 0.15 | Renewable needed W/sf | 0.1255 | 0.11136 | 0.12462 | 0.12833 | 0.125 | 0.082812 | 0.037 | 0.095238 | 0.11364 | 0.06 | 0.13684 | 0.084667 | 0.05 | 0.084706 | 0.0625 | 0.038462 | 0.029375 | 0.075 | 0.05 | 1.5
| 0.3 |  | 0.121 | 0.10455 | 0.11077 | 0.12333 | 0.11923 | 0.078125 | 0.034 | 0.095238 | 0.11364 | 0.06 | 0.13684 | 0.082667 | 0.05 | 0.081176 | 0.0625 | 0.038462 | 0.0275 | 0.075 | 0.05
| 0.5 |  | 0.115 | 0.095455 | 0.092308 | 0.11667 | 0.11154 | 0.071875 | 0.03 | 0.095238 | 0.11364 | 0.06 | 0.13684 | 0.08 | 0.05 | 0.076471 | 0.0625 | 0.038462 | 0.025 | 0.075 | 0.05
| 0.7 | Agreed to adjustment | 0.109 | 0.086364 | 0.073846 | 0.11 | 0.10385 | 0.065625 | 0.026 | 0.095238 | 0.11364 | 0.06 | 0.13684 | 0.077333 | 0.05 | 0.071765 | 0.0625 | 0.038462 | 0.0225 | 0.075 | 0.05
| 1 |  | 0.1 | 0.072727 | 0.046154 | 0.1 | 0.092308 | 0.05625 | 0.02 | 0.095238 | 0.11364 | 0.06 | 0.13684 | 0.073333 | 0.05 | 0.064706 | 0.0625 | 0.038462 | 0.01875 | 0.075 | 0.05

## Carry-overCurrentPC-1.25x
Carryover analysis for base code proposal
Alternate reasonable measure selections without improvements above minimum regulated equipment efficiency
| Selections w/o improved equip. efficiency |  | R-2/4, I-1 | I-2 | R-1 | B | A-2 | M | E | S-1/2
| ID | Measure | MF | Health | Hotel | Office | Rest | Retail | School | Whse | Other
| E03 | Envelope Leakage Reduction | Y | Y | Y | Y | Y | Y | Y | Y | Y
| E04 | Add R-5 Roof Insulation | Y | Y | Y | Y | Y | Y | Y | Y | Y | R-10 in CZ 8
| E05 | Add R-2.5 ci Wall Insulation | Y | Y | Y | Y | Y | Y | Y | Y | Y | R-5 in CZ 8
| E06 | Improve Fenestration | Y | Y | Y | Y | Y | Y | Y | Y | Y
| H04 | Residential HVAC control. | Y
| W01 | SHW preheat recovery |  | 30% | [7 empty] | of SHW load
| W02 | Heat pump water heater |  |  | 30% |  | 30% |  |  |  |  | of SHW load
| W04 | SHW pipe insulation |  |  |  |  | Y | Y | Y |  | Y
| W05 | Point of use water heaters |  |  |  | Y |  |  | Y
| W06 | Thermostatic balancing valves | N | [10 empty] | << removed to allow individual apartment water heaters
| W07 | SHW heat trace system |  | Y | Y
| W09 | SHW flow reduction | Y |  | Y
| L04 | Increase daylight area |  |  |  | 5% |  | 10% |  | 5% |  | of floor area |  | << reduced to match a more broad array of building configurations
| L05 | Residential light control | Y
| L06 | Lighting power reduction | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | 10% | of LPD
| Q01 | Efficient Elevator |  | Y | Y | Y | N | [6 empty] | << removed as elevators less likely in restaurants
| Q02 | Efficient Commercial Kitchen Equipment |  |  |  |  | Y
| Q04 | Fault detection |  | Y | Y | Y | Y | Y | Y | Y | Y
Energy Efficiency Credits Achieved by reasonable package without equipment efficiency improvement
| Use group and building type |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
| R-2, R-4, I-1 | Multi-family/Dormitory | 71.5 | 66.5 | 68.5 | 80.5 | 82 | 103.5 | 97 | 79.5 | 96 | 120.5 | 93 | 97 | 130.5 | 121 | 95.5 | 144.5 | 140.5 | 124.5 | 138
| I-2 | Healthcare | 29.5 | 30 | 29 | 31 | 32.5 | 36.5 | 39 | 32.5 | 33.5 | 39.5 | 33 | 36 | 39.5 | 30.5 | 28 | 38.5 | 35 | 42.5 | 30
| R-1 | Hotel/Motel | 58.5 | 59.5 | 60 | 63.5 | 53.5 | 68.5 | 66.5 | 62 | 66.5 | 80 | 65.5 | 70 | 91.5 | 72.5 | 74 | 102.5 | 87 | 96 | 87
| B | Office Buildings | 57.5 | 59 | 61 | 60.5 | 62 | 61 | 68 | 56 | 56.5 | 67 | 53.5 | 61 | 72.5 | 59 | 53.5 | 86 | 76 | 78 | 64
| A-2 | Restaurant Buildings | 54 | 56 | 60 | 59 | 64 | 68.5 | 78.5 | 71 | 73 | 87.5 | 72 | 76.5 | 96 | 76 | 73.5 | 101 | 93 | 88.5 | 68
| M | Retail Buildings | 99 | 98.5 | 97.5 | 103.5 | 86 | 91 | 106.5 | 94 | 91 | 120 | 89.5 | 93.5 | 124 | 93 | 81 | 134.5 | 121 | 111 | 103
| E | Education Buildings | 45.5 | 46.5 | 39 | 44.5 | 43 | 45.5 | 55 | 44.5 | 36 | 54 | 42 | 51 | 59.5 | 54 | 59.5 | 73 | 69.5 | 56.5 | 73
| S-1, S-2 | Warehouse | 71 | 69.5 | 74.5 | 76 | 69.5 | 72.5 | 91.5 | 73.5 | 67 | 121 | 70.5 | 76.5 | 128.5 | 70 | 69 | 124.5 | 109.5 | 103.5 | 75
| Other | Other | 41 | 39.5 | 38 | 39.5 | 35.5 | 40 | 48 | 35.5 | 30 | 59 | 36 | 39.5 | 66 | 41.5 | 36.5 | 76 | 64.5 | 61.5 | 56
Requirements with PNNL PCs
Min of
5 |  | Building Use Type | Climate Zone
% of Req'd |  |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
4.932% | R-2, R-4, I-1 | Multi-family/Dormitory | 81.25 | 82.5 | 83.75 | 96.25 | 100 | 107.5 | 100 | 101.25 | 112.5 | 107.5 | 112.5 | 112.5 | 107.5 | 112.5 | 112.5 | 87.5 | 111.25 | 100 | 97.5
9.987% | I-2 | Healthcare | 53.75 | 52.5 | 47.5 | 46.25 | 45 | 47.5 | 40 | 40 | 37.5 | 45 | 45 | 43.75 | 53.75 | 53.75 | 55 | 57.5 | 58.75 | 62.5 | 66.25
5.09% | R-1 | Hotel/Motel | 78.75 | 77.5 | 82.5 | 81.25 | 87.5 | 88.75 | 96.25 | 100 | 105 | 101.25 | 103.75 | 110 | 106.25 | 107.5 | 112.5 | 103.75 | 108.75 | 108.75 | 106.25
5.81% | B | Office Buildings | 77.5 | 77.5 | 80 | 82.5 | 82.5 | 81.25 | 80 | 80 | 85 | 87.5 | 90 | 92.5 | 88.75 | 91.25 | 96.25 | 88.75 | 92.5 | 92.5 | 88.75
5.706% | A-2 | Restaurant Buildings | 87.5 | 87.5 | 90 | 90 | 93.75 | 93.75 | 87.5 | 91.25 | 102.5 | 86.25 | 92.5 | 97.5 | 83.75 | 90 | 97.5 | 75 | 83.75 | 71.25 | 63.75
5.464% | M | Retail Buildings | 100 | 98.75 | 103.75 | 98.75 | 101.25 | 105 | 83.75 | 92.5 | 108.75 | 100 | 82.5 | 81.25 | 98.75 | 77.5 | 62.5 | 93.75 | 83.75 | 93.75 | 72.5
6.546% | E | School/Education Buildings | 70 | 71.25 | 68.75 | 72.5 | 72.5 | 71.25 | 73.75 | 77.5 | 73.75 | 76.25 | 82.5 | 77.5 | 80 | 83.75 | 83.75 | 81.25 | 83.75 | 78.75 | 72.5
5.638% | S-1, S-2 | Warehouse and Semiheated | 76.25 | 75 | 76.25 | 75 | 72.5 | 71.25 | 55 | 67.5 | 77.5 | 106.25 | 85 | 93.75 | 112.5 | 102.5 | 90 | 112.5 | 111.25 | 112.5 | 112.5
11.78% | Other | Other | 38.75 | 38.75 | 38.75 | 40 | 40 | 41.25 | 37.5 | 40 | 45 | 43.75 | 43.75 | 43.75 | 46.25 | 45 | 45 | 45 | 46.25 | 45 | 42.5
6.773%
Carryover surplus load management points needed with no increases in regulated equipment efficiency
| Use group and building type |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
| R-2, R-4, I-1 | Multi-family/Dormitory | 10 | 16 | 16 | 16 | 18 | 4 | 3 | 22 | 17 | -13 | 20 | 16 | -23 | -9 | 17 | -57 | -30 | -25 | -41
| I-2 | Healthcare | 25 | 23 | 19 | 16 | 13 | 11 | 1 | 8 | 4 | 6 | 12 | 8 | 15 | 24 | 27 | 19 | 24 | 20 | 37
| R-1 | Hotel/Motel | 21 | 18 | 23 | 18 | 34 | 21 | 30 | 38 | 39 | 22 | 39 | 40 | 15 | 35 | 39 | 2 | 22 | 13 | 20
| B | Office Buildings | 20 | 19 | 19 | 22 | 21 | 21 | 12 | 24 | 29 | 21 | 37 | 32 | 17 | 33 | 43 | 3 | 17 | 15 | 25
| A-2 | Restaurant Buildings | 34 | 32 | 30 | 31 | 30 | 26 | 9 | 21 | 30 | -2 | 21 | 21 | -13 | 14 | 24 | -26 | -10 | -18 | -5
| M | Retail Buildings | 1 | 1 | 7 | -5 | 16 | 14 | -23 | -2 | 18 | -20 | -7 | -13 | -26 | -16 | -19 | -41 | -38 | -18 | -31
| E | Education Buildings | 25 | 25 | 30 | 28 | 30 | 26 | 19 | 33 | 38 | 23 | 41 | 27 | 21 | 30 | 25 | 9 | 15 | 23 | -1
| S-1, S-2 | Warehouse | 6 | 6 | 2 | -1 | 3 | -2 | -37 | -6 | 11 | -15 | 15 | 18 | -16 | 33 | 21 | -12 | 2 | 9 | 38
| Other | Other | -3 | -1 | 1 | 1 | 5 | 2 | -11 | 5 | 15 | -16 | 8 | 5 | -20 | 4 | 9 | -31 | -19 | -17 | -14
|  | Minimum Carryover Credit | 5 |  |  |  | Roundoff Carryover Credit adder | 2
| Carryover surplus load management points allowed | [5 empty] | Table C406.1.1(2)
% of Req'd | Use group and building type |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
12.15% | R-2, R-4, I-1 | Multi-family/Dormitory | 12 | 18 | 18 | 18 | 20 | 6 | 5 | 24 | 19 | 5 | 22 | 18 | 5 | 5 | 19 | 5 | 5 | 5 | 5
37% | I-2 | Healthcare | 27 | 25 | 21 | 18 | 15 | 13 | 5 | 10 | 6 | 8 | 14 | 10 | 17 | 26 | 29 | 21 | 26 | 22 | 39
28.29% | R-1 | Hotel/Motel | 23 | 20 | 25 | 20 | 36 | 23 | 32 | 40 | 41 | 24 | 41 | 42 | 17 | 37 | 41 | 5 | 24 | 15 | 22
28.62% | B | Office Buildings | 22 | 21 | 21 | 24 | 23 | 23 | 14 | 26 | 31 | 23 | 39 | 34 | 19 | 35 | 45 | 5 | 19 | 17 | 27
22.76% | A-2 | Restaurant Buildings | 36 | 34 | 32 | 33 | 32 | 28 | 11 | 23 | 32 | 5 | 23 | 23 | 5 | 16 | 26 | 5 | 5 | 5 | 5
7.937% | M | Retail Buildings | 5 | 5 | 9 | 5 | 18 | 16 | 5 | 5 | 20 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
35.07% | E | Education Buildings | 27 | 27 | 32 | 30 | 32 | 28 | 21 | 35 | 40 | 25 | 43 | 29 | 23 | 32 | 27 | 11 | 17 | 25 | 5
13.35% | S-1, S-2 | Warehouse | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 13 | 5 | 17 | 20 | 5 | 35 | 23 | 5 | 5 | 11 | 40
15.5% | Other | Other | 5 | 5 | 5 | 5 | 7 | 5 | 5 | 7 | 17 | 5 | 10 | 7 | 5 | 6 | 11 | 5 | 5 | 5 | 5
22.3%
7.359% | 33% | of recent new construction has fossil fuels, so impact on energy credits is | [21 empty] | PV Credits for 0.1 W/sf
0.6623% | 9% | Maximum energy credits showing small % of total building energy use
PV W/sf required to meet carry-over need with no LM carry over
| Use group and building type |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8 |  |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
| R-2, R-4, I-1 | Multi-family/Dormitory | 0.11111 | 0.10667 | 0.14545 | 0.094118 | 0.1 | 0.02 | 0.015789 | 0.10476 | 0.13077 | 0 | 0.15385 | 0.17778 | 0 | 0 | 0.17 | 0 | 0 | 0 | 0 | 1.5 | Multi-family/Dormitory | 9 | 15 | 11 | 17 | 18 | 20 | 19 | 21 | 13 | 10 | 13 | 9 | 9 | 11 | 10 | 9 | 10 | 9 | 7
| I-2 | Healthcare | 0.41667 | 0.38333 | 0.31667 | 0.26667 | 0.21667 | 0.1375 | 0.014286 | 0.088889 | 0.05 | 0.1 | 0.15 | 0.13333 | 0.25 | 0.34286 | 0.38571 | 0.31667 | 0.34286 | 0.4 | 0.925 |  | Healthcare | 6 | 6 | 6 | 6 | 6 | 8 | 7 | 9 | 8 | 6 | 8 | 6 | 6 | 7 | 7 | 6 | 7 | 5 | 4
| R-1 | Hotel/Motel | 0.23333 | 0.225 | 0.19167 | 0.2 | 0.30909 | 0.19091 | 0.3 | 0.31667 | 0.3 | 0.24444 | 0.325 | 0.5 | 0.16667 | 0.31818 | 0.43333 | 0.025 | 0.24444 | 0.18571 | 0.4 |  | Hotel/Motel | 9 | 8 | 12 | 9 | 11 | 11 | 10 | 12 | 13 | 9 | 12 | 8 | 9 | 11 | 9 | 8 | 9 | 7 | 5
| B | Office Buildings | 0.14286 | 0.13571 | 0.11176 | 0.14667 | 0.12353 | 0.11053 | 0.066667 | 0.10909 | 0.12083 | 0.12353 | 0.16818 | 0.2 | 0.12143 | 0.18333 | 0.23889 | 0.021429 | 0.1 | 0.10714 | 0.22727 |  | Office | 14 | 14 | 17 | 15 | 17 | 19 | 18 | 22 | 24 | 17 | 22 | 16 | 14 | 18 | 18 | 14 | 17 | 14 | 11
| A-2 | Restaurant Buildings | 1.7 | 1.6 | 1.5 | 1.55 | 1.5 | 1.3 | 0.45 | 0.7 | 0.75 | 0 | 0.7 | 1.05 | 0 | 0.46667 | 1.2 | 0 | 0 | 0 | 0 |  | Restaurant | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 4 | 2 | 3 | 2 | 2 | 3 | 2 | 2 | 2 | 2 | 1
| M | Retail Buildings | 0.0125 | 0.0125 | 0.058333 | 0 | 0.14545 | 0.11667 | 0 | 0 | 0.10588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Retail | 8 | 8 | 12 | 9 | 11 | 12 | 12 | 17 | 17 | 11 | 13 | 9 | 10 | 11 | 10 | 9 | 10 | 9 | 6
| E | Education Buildings | 0.25 | 0.22727 | 0.23077 | 0.23333 | 0.23077 | 0.1625 | 0.12667 | 0.15714 | 0.17273 | 0.15333 | 0.21579 | 0.18 | 0.15 | 0.17647 | 0.15625 | 0.069231 | 0.09375 | 0.19167 | 0 |  | School/Education | 10 | 11 | 13 | 12 | 13 | 16 | 15 | 21 | 22 | 15 | 19 | 15 | 14 | 17 | 16 | 13 | 16 | 12 | 10
| S-1, S-2 | Warehouse | 0.015789 | 0.016216 | 0.0036364 | 0 | 0.0056604 | 0 | 0 | 0 | 0.016667 | 0 | 0.026786 | 0.047368 | 0 | 0.080488 | 0.058333 | 0 | 0.00625 | 0.03913 | 0.2375 |  | Warehouse | 38 | 37 | 55 | 45 | 53 | 53 | 49 | 58 | 66 | 36 | 56 | 38 | 29 | 41 | 36 | 24 | 32 | 23 | 16
Load Management Points available for carryover net of revised (lowered) requirement (CED1-188)
Surplus LM (G01,G02,G06) after meet LM/PV requirements with only LM
| Building Occupancy Group |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | SA | SB | SC | 6A | 6B | 7 | 8
| R-2, R-4, and 1-1 | Multi-family/Dormitory | 41 | 28 | 18 | 19 | 6 | 16 | 12 | 6 | 24 | 16 | 26 | 27 | 21 | 19 | 23 | 10 | 12 | 15 | 20
| I-2 | Healthcare | 2 | 3 | 2 | 2 | 0 | 9 | 0 | -4 | 1 | 3 | 6 | 4 | 4 | 4 | 3 | 4 | 1 | 3 | 3
| R-1 | Hotel/Motel | 7 | 9 | 4 | 8 | 6 | 7 | 9 | 6 | 5 | 11 | 6 | 15 | 10 | 7 | 13 | 10 | 10 | 11 | 14
| B | Office Buildings | -23 | -13 | -18 | -15 | -19 | -29 | -21 | -25 | -33 | -15 | -29 | -14 | -12 | -19 | -16 | -14 | -18 | -12 | -14
| A-2 | Restaurant Buildings | 41 | 35 | 48 | 38 | 42 | 38 | 39 | 33 | 34 | 32 | 28 | 29 | 31 | 25 | 24 | 27 | 26 | 24 | 12
| M | Retail Buildings | -13 | -13 | -4 | 0 | -3 | -14 | -5 | -9 | -16 | 5 | -7 | 10 | 1 | 1 | 11 | 0 | 1 | 4 | -6
| E | Education Buildings | 3 | 5 | 12 | 4 | 5 | 5 | 3 | -9 | -16 | 0 | 0 | 2 | -1 | 4 | -12 | -1 | 2 | -1 | -5
| S-1 and S-2 | Warehouse | -55 | -15 | -18 | -22 | -26 | -16 | -21 | -27 | -28 | -33 | -42 | -37 | -39 | -51 | -53 | -32 | -54 | -34 | -27
| All Other |  | 9 | 7 | 2 | 4 | -1 | -2 | -2 | -7 | -11 | 3 | -4 | 4 | 3 | -1 | -2 | 1 | -1 | 3 | -1
Restaurant Building example
|  | Carryover Needed | 36 | 34 | 32 | 33 | 32 | 28 | 11 | 23 | 32 | 5 | 23 | 23 | 5 | 16 | 26 | 5 | 5 | 5 | 5
|  | Surplus LM Points (No PV) | 41 | 35 | 48 | 38 | 42 | 38 | 39 | 33 | 34 | 32 | 28 | 29 | 31 | 25 | 24 | 27 | 26 | 24 | 12
| 0.15 | LM Credits applyable | 6.15 | 5.25 | 7.2 | 5.7 | 6.3 | 5.7 | 5.85 | 4.95 | 5.1 | 4.8 | 4.2 | 4.35 | 4.65 | 3.75 | 3.6 | 4.05 | 3.9 | 3.6 | 1.8
| 0.3 |  | 12.3 | 10.5 | 14.4 | 11.4 | 12.6 | 11.4 | 11 | 9.9 | 10.2 | 5 | 8.4 | 8.7 | 5 | 7.5 | 7.2 | 5 | 5 | 5 | 3.6
| 0.5 |  | 20.5 | 17.5 | 24 | 19 | 21 | 19 | 11 | 16.5 | 17 | 5 | 14 | 14.5 | 5 | 12.5 | 12 | 5 | 5 | 5 | 5
| 0.7 | Agreed to adjustment | 28.7 | 24.5 | 32 | 26.6 | 29.4 | 26.6 | 11 | 23 | 23.8 | 5 | 19.6 | 20.3 | 5 | 16 | 16.8 | 5 | 5 | 5 | 5
| 1 |  | 36 | 34 | 32 | 33 | 32 | 28 | 11 | 23 | 32 | 5 | 23 | 23 | 5 | 16 | 24 | 5 | 5 | 5 | 5
|  |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
|  | Renewable Credits per 0.1 W/sf | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 4 | 2 | 3 | 2 | 2 | 3 | 2 | 2 | 2 | 2 | 1
| 0.15 | Renewable needed W/sf | 1.4925 | 1.4375 | 1.24 | 1.365 | 1.285 | 1.115 | 0.2575 | 0.60167 | 0.6725 | 0.01 | 0.62667 | 0.9325 | 0.0175 | 0.40833 | 1.12 | 0.0475 | 0.055 | 0.07 | 0.32 | 1.5
| 0.3 |  | 1.185 | 1.175 | 0.88 | 1.08 | 0.97 | 0.83 | 0 | 0.43667 | 0.545 | 0 | 0.48667 | 0.715 | 0 | 0.28333 | 0.94 | 0 | 0 | 0 | 0.14
| 0.5 |  | 0.775 | 0.825 | 0.4 | 0.7 | 0.55 | 0.45 | 0 | 0.21667 | 0.375 | 0 | 0.3 | 0.425 | 0 | 0.11667 | 0.7 | 0 | 0 | 0 | 0
| 0.7 | Agreed to adjustment | 0.365 | 0.475 | 0 | 0.32 | 0.13 | 0.07 | 0 | 0 | 0.205 | 0 | 0.11333 | 0.135 | 0 | 0 | 0.46 | 0 | 0 | 0 | 0
| 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0
Health building example
|  | Carryover Needed | 27 | 25 | 21 | 18 | 15 | 13 | 5 | 10 | 6 | 8 | 14 | 10 | 17 | 26 | 29 | 21 | 26 | 22 | 39
|  | Surplus LM Points (No PV) | 2 | 3 | 2 | 2 | 0 | 9 | 0 | -4 | 1 | 3 | 6 | 4 | 4 | 4 | 3 | 4 | 1 | 3 | 3
| 0.15 | LM Credits applyable | 0.3 | 0.45 | 0.3 | 0.3 | 0 | 1.35 | 0 | 0 | 0.15 | 0.45 | 0.9 | 0.6 | 0.6 | 0.6 | 0.45 | 0.6 | 0.15 | 0.45 | 0.45
| 0.3 |  | 0.6 | 0.9 | 0.6 | 0.6 | 0 | 2.7 | 0 | 0 | 0.3 | 0.9 | 1.8 | 1.2 | 1.2 | 1.2 | 0.9 | 1.2 | 0.3 | 0.9 | 0.9
| 0.5 |  | 1 | 1.5 | 1 | 1 | 0 | 4.5 | 0 | 0 | 0.5 | 1.5 | 3 | 2 | 2 | 2 | 1.5 | 2 | 0.5 | 1.5 | 1.5
| 0.7 | Agreed to adjustment | 1.4 | 2.1 | 1.4 | 1.4 | 0 | 6.3 | 0 | 0 | 0.7 | 2.1 | 4.2 | 2.8 | 2.8 | 2.8 | 2.1 | 2.8 | 0.7 | 2.1 | 2.1
| 1 |  | 2 | 3 | 2 | 2 | 0 | 9 | 0 | 0 | 1 | 3 | 6 | 4 | 4 | 4 | 3 | 4 | 1 | 3 | 3
|  |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
|  | Renewable Credits per 0.1 W/sf | 6 | 6 | 6 | 6 | 6 | 8 | 7 | 9 | 8 | 6 | 8 | 6 | 6 | 7 | 7 | 6 | 7 | 5 | 4
| 0.15 | Renewable needed W/sf | 0.445 | 0.40917 | 0.345 | 0.295 | 0.25 | 0.14563 | 0.071429 | 0.11111 | 0.073125 | 0.12583 | 0.16375 | 0.15667 | 0.27333 | 0.36286 | 0.40786 | 0.34 | 0.36929 | 0.431 | 0.96375 | 1.5
| 0.3 |  | 0.44 | 0.40167 | 0.34 | 0.29 | 0.25 | 0.12875 | 0.071429 | 0.11111 | 0.07125 | 0.11833 | 0.1525 | 0.14667 | 0.26333 | 0.35429 | 0.40143 | 0.33 | 0.36714 | 0.422 | 0.9525
| 0.5 |  | 0.43333 | 0.39167 | 0.33333 | 0.28333 | 0.25 | 0.10625 | 0.071429 | 0.11111 | 0.06875 | 0.10833 | 0.1375 | 0.13333 | 0.25 | 0.34286 | 0.39286 | 0.31667 | 0.36429 | 0.41 | 0.9375
| 0.7 | Agreed to adjustment | 0.42667 | 0.38167 | 0.32667 | 0.27667 | 0.25 | 0.08375 | 0.071429 | 0.11111 | 0.06625 | 0.098333 | 0.1225 | 0.12 | 0.23667 | 0.33143 | 0.38429 | 0.30333 | 0.36143 | 0.398 | 0.9225
| 1 |  | 0.41667 | 0.36667 | 0.31667 | 0.26667 | 0.25 | 0.05 | 0.071429 | 0.11111 | 0.0625 | 0.083333 | 0.1 | 0.1 | 0.21667 | 0.31429 | 0.37143 | 0.28333 | 0.35714 | 0.38 | 0.9
Education Building example
|  | Carryover Needed | 27 | 27 | 32 | 30 | 32 | 28 | 21 | 35 | 40 | 25 | 43 | 29 | 23 | 32 | 27 | 11 | 17 | 25 | 5
|  | Surplus LM Points (No PV) | 3 | 5 | 12 | 4 | 5 | 5 | 3 | -9 | -16 | 0 | 0 | 2 | -1 | 4 | -12 | -1 | 2 | -1 | -5
| 0.15 | LM Credits applyable | 0.45 | 0.75 | 1.8 | 0.6 | 0.75 | 0.75 | 0.45 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0.6 | 0 | 0 | 0.3 | 0 | 0
| 0.3 |  | 0.9 | 1.5 | 3.6 | 1.2 | 1.5 | 1.5 | 0.9 | 0 | 0 | 0 | 0 | 0.6 | 0 | 1.2 | 0 | 0 | 0.6 | 0 | 0
| 0.5 |  | 1.5 | 2.5 | 6 | 2 | 2.5 | 2.5 | 1.5 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 0 | 1 | 0 | 0
| 0.7 | Agreed to adjustment | 2.1 | 3.5 | 8.4 | 2.8 | 3.5 | 3.5 | 2.1 | 0 | 0 | 0 | 0 | 1.4 | 0 | 2.8 | 0 | 0 | 1.4 | 0 | 0
| 1 |  | 3 | 5 | 12 | 4 | 5 | 5 | 3 | 0 | 0 | 0 | 0 | 2 | 0 | 4 | 0 | 0 | 2 | 0 | 0
|  |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
|  | Renewable Credits per 0.1 W/sf | 10 | 11 | 13 | 12 | 13 | 16 | 15 | 21 | 22 | 15 | 19 | 15 | 14 | 17 | 16 | 13 | 16 | 12 | 10
| 0.15 | Renewable needed W/sf | 0.2655 | 0.23864 | 0.23231 | 0.245 | 0.24038 | 0.17031 | 0.137 | 0.16667 | 0.18182 | 0.16667 | 0.22632 | 0.19133 | 0.16429 | 0.18471 | 0.16875 | 0.084615 | 0.10437 | 0.20833 | 0.05 | 1.5
| 0.3 |  | 0.261 | 0.23182 | 0.21846 | 0.24 | 0.23462 | 0.16562 | 0.134 | 0.16667 | 0.18182 | 0.16667 | 0.22632 | 0.18933 | 0.16429 | 0.18118 | 0.16875 | 0.084615 | 0.1025 | 0.20833 | 0.05
| 0.5 |  | 0.255 | 0.22273 | 0.2 | 0.23333 | 0.22692 | 0.15937 | 0.13 | 0.16667 | 0.18182 | 0.16667 | 0.22632 | 0.18667 | 0.16429 | 0.17647 | 0.16875 | 0.084615 | 0.1 | 0.20833 | 0.05
| 0.7 | Agreed to adjustment | 0.249 | 0.21364 | 0.18154 | 0.22667 | 0.21923 | 0.15313 | 0.126 | 0.16667 | 0.18182 | 0.16667 | 0.22632 | 0.184 | 0.16429 | 0.17176 | 0.16875 | 0.084615 | 0.0975 | 0.20833 | 0.05
| 1 |  | 0.24 | 0.2 | 0.15385 | 0.21667 | 0.20769 | 0.14375 | 0.12 | 0.16667 | 0.18182 | 0.16667 | 0.22632 | 0.18 | 0.16429 | 0.16471 | 0.16875 | 0.084615 | 0.09375 | 0.20833 | 0.05

## BASEdeficit
BASE STANDARD | [6 empty] | Table C406.1.1(2)
Carryover surplus load management DEFICIT from points allowed in PD2, if fossil fuel space or water heating equipment used
| Use group and building type |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
| R-2, R-4, I-1 | Multi-family/Dormitory | 16 | 15 | 17 | 15 | 17 | 18 | 19 | 20 | 21 | 19 | 21 | 22 | 12 | 21 | 23 | 0 | 19 | 10 | 17
| I-2 | Healthcare | 15 | 16 | 16 | 16 | 17 | 17 | 9 | 16 | 17 | 18 | 18 | 19 | 14 | 19 | 19 | 0 | 14 | 12 | 18
| R-1 | Hotel/Motel | 18 | 18 | 18 | 18 | 19 | 19 | 6 | 18 | 21 | 0 | 18 | 18 | 0 | 11 | 19 | 0 | 0 | 0 | 0
| B | Office Buildings | 0 | 0 | 4 | 0 | 13 | 11 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| A-2 | Restaurant Buildings | 14 | 14 | 14 | 14 | 15 | 14 | 15 | 15 | 15 | 16 | 17 | 16 | 16 | 17 | 17 | 6 | 12 | 16 | 0
| M | Retail Buildings | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 12 | 15 | 0 | 21 | 18 | 0 | 0 | 6 | 23
| E | Education Buildings | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 9 | 0 | 5 | 2 | 0 | 1 | 6 | 0 | 0 | 0 | 0
| S-1, S-2 | Warehouse | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 87 | 5 | 5 | 5 | 4 | 6 | 5 | 4 | 5 | 7 | 3 | 6 | 6 | 3 | 6 | 6 | 1 | 3 | 4 | 3
|  | 57.24% | 0.625 | 0.625 | 0.625 | 0.5 | 0.75 | 0.625 | 0.5 | 0.625 | 0.875 | 0.375 | 0.75 | 0.75 | 0.375 | 0.75 | 0.75 | 0.125 | 0.375 | 0.5 | 0.375

## Carry-overForCD
Carryover analysis for Appendix CF "Advanced Energy Credit Package" requirements
Changes for advanced package from base package highlighted
CF/CD: | Alternate high efficiency measure selections without regulated equipment above minimum (Appendix CD/CF)
| Selections w/o improved equip. efficiency |  | R-2/4, I-1 | I-2 | R-1 | B | A-2 | M | E | S-1/2
| ID | Measure | MF | Health | Htl | Ofc | Rest | Rtl | Sch | Whse | Other
| E03 | Envelope Leakage Reduction | Y | Y | Y | Y | Y | Y | Y | Y | Y
| E04 | Add R-10 Roof Insulation | Y | Y | Y | Y | Y | Y | Y | Y | Y
| E05 | Add R-5ci Wall Insulation | Y | Y | Y | Y | Y | Y | Y | Y | Y
| E06 | Improve Fenestration | Y | Y | Y | Y | Y | Y | Y | Y | Y
| H04 | Residential HVAC control. | Y
| W01 | SHW preheat recovery |  | 30% | 30% | [6 empty] | of SHW load
| W02 | Heat pump water heater |  |  | 30% |  | 60% |  |  |  |  | of SHW load
| W04 | SHW pipe insulation |  | Y | Y |  | Y | Y | Y |  | Y
| W05 | Point of use water heaters |  |  |  | Y |  |  | Y
| W06 | Thermostatic balancing valves |  | Y
| W07 | SHW heat trace system |  |  | Y
| W09 | SHW flow reduction | Y |  | Y
| L02 | Lighting high end trim |  | Y |  | Y |  |  | Y
| L03 | Increase occupancy sensor
| L04 | Increase daylight area |  |  |  | 10% |  | 20% |  | 20% |  | of floor area
| L05 | Residential light control | Y
| L06 | Lighting power reduction | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | of LPD
| Q01 | Efficient Elevator |  | Y | Y | Y
| Q02 | Efficient Commercial Kitchen Equipment |  |  |  |  | Y
| Q04 | Fault detection |  | Y | Y | Y | Y | Y | Y | Y | Y
Energy Efficiency Credits Achieved by reasonable package without equipment efficiency improvement
| Use group and building type |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
| R-2, R-4, I-1 | Multi-family/Dormitory | 81 | 76 | 76 | 89 | 89 | 111 | 107 | 87 | 101 | 129 | 100 | 103 | 141 | 129 | 101 | 157 | 152 | 136 | 140
| I-2 | Healthcare | 50 | 52 | 49 | 53 | 54 | 59 | 64 | 56 | 59 | 62 | 55 | 60 | 60 | 51 | 48 | 56 | 52 | 57 | 39
| R-1 | Hotel/Motel | 88 | 94 | 92 | 103 | 85 | 102 | 105 | 99 | 103 | 120 | 105 | 115 | 135 | 113 | 121 | 146 | 130 | 139 | 124
| B | Office Buildings | 91 | 93 | 96 | 97 | 95 | 94 | 103 | 89 | 91 | 97 | 84 | 93 | 100 | 87 | 84 | 112 | 104 | 104 | 77
| A-2 | Restaurant Buildings | 76 | 79 | 85 | 84 | 92 | 99 | 112 | 104 | 109 | 119 | 105 | 112 | 128 | 110 | 110 | 130 | 126 | 116 | 92
| M | Retail Buildings | 183 | 184 | 182 | 194 | 158 | 168 | 181 | 173 | 173 | 181 | 161 | 161 | 177 | 160 | 141 | 186 | 180 | 167 | 129
| E | Education Buildings | 69 | 73 | 62 | 73 | 69 | 74 | 88 | 73 | 64 | 84 | 69 | 79 | 88 | 82 | 91 | 102 | 101 | 82 | 79
| S-1, S-2 | Warehouse | 160 | 157 | 174 | 172 | 166 | 168 | 173 | 170 | 173 | 170 | 148 | 149 | 165 | 126 | 140 | 153 | 151 | 140 | 94
| Other | Other | 65 | 65 | 61 | 64 | 56 | 61 | 71 | 58 | 50 | 77 | 56 | 59 | 83 | 59 | 56 | 93 | 82 | 77 | 60
Appendis CD: Requirements are 1.5 of final table; based here on Current-PNNL-PC-requirements
Min of |  |  |  | 1.5
5 |  | Building Use Type | Climate Zone
% of Req'd |  |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8 | Avg
4.11% | R-2, R-4, I-1 | Multi-family/Dormitory | 97.5 | 99 | 100.5 | 115.5 | 120 | 129 | 120 | 121.5 | 135 | 129 | 135 | 135 | 129 | 135 | 135 | 105 | 133.5 | 120 | 117 | 121.6579
8.322% | I-2 | Healthcare | 64.5 | 63 | 57 | 55.5 | 54 | 57 | 48 | 48 | 45 | 54 | 54 | 52.5 | 64.5 | 64.5 | 66 | 69 | 70.5 | 75 | 79.5 | 60.0789
4.242% | R-1 | Hotel/Motel | 94.5 | 93 | 99 | 97.5 | 105 | 106.5 | 115.5 | 120 | 126 | 121.5 | 124.5 | 132 | 127.5 | 129 | 135 | 124.5 | 130.5 | 130.5 | 127.5 | 117.8684
4.842% | B | Office Buildings | 93 | 93 | 96 | 99 | 99 | 97.5 | 96 | 96 | 102 | 105 | 108 | 111 | 106.5 | 109.5 | 115.5 | 106.5 | 111 | 111 | 106.5 | 103.2632
4.755% | A-2 | Restaurant Buildings | 105 | 105 | 108 | 108 | 112.5 | 112.5 | 105 | 109.5 | 123 | 103.5 | 111 | 117 | 100.5 | 108 | 117 | 90 | 100.5 | 85.5 | 76.5 | 105.1579
4.553% | M | Retail Buildings | 120 | 118.5 | 124.5 | 118.5 | 121.5 | 126 | 100.5 | 111 | 130.5 | 120 | 99 | 97.5 | 118.5 | 93 | 75 | 112.5 | 100.5 | 112.5 | 87 | 109.8158
5.455% | E | School/Education Buildings | 84 | 85.5 | 82.5 | 87 | 87 | 85.5 | 88.5 | 93 | 88.5 | 91.5 | 99 | 93 | 96 | 100.5 | 100.5 | 97.5 | 100.5 | 94.5 | 87 | 91.6579
4.698% | S-1, S-2 | Warehouse and Semiheated | 91.5 | 90 | 91.5 | 90 | 87 | 85.5 | 66 | 81 | 93 | 127.5 | 102 | 112.5 | 135 | 123 | 108 | 135 | 133.5 | 135 | 135 | 106.4211
9.819% | Other | Other | 46.5 | 46.5 | 46.5 | 48 | 48 | 49.5 | 45 | 48 | 54 | 52.5 | 52.5 | 52.5 | 55.5 | 54 | 54 | 54 | 55.5 | 54 | 51 | 50.9211
5.644%
Carryover surplus load management points needed with no increases in regulated equipment efficiency
| Use group and building type |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
| R-2, R-4, I-1 | Multi-family/Dormitory | 17 | 23 | 25 | 27 | 31 | 18 | 13 | 35 | 34 | 0 | 35 | 32 | -12 | 6 | 34 | -52 | -19 | -16 | -23
| I-2 | Healthcare | 15 | 11 | 8 | 3 | 0 | -2 | -16 | -8 | -14 | -8 | -1 | -8 | 5 | 14 | 18 | 13 | 19 | 18 | 41
| R-1 | Hotel/Motel | 7 | -1 | 7 | -6 | 20 | 5 | 11 | 21 | 23 | 2 | 20 | 17 | -8 | 16 | 14 | -22 | 1 | -9 | 4
| B | Office Buildings | 2 | 0 | 0 | 2 | 4 | 4 | -7 | 7 | 11 | 8 | 24 | 18 | 7 | 23 | 32 | -6 | 7 | 7 | 30
| A-2 | Restaurant Buildings | 29 | 26 | 23 | 24 | 21 | 14 | -7 | 6 | 14 | -16 | 6 | 5 | -28 | -2 | 7 | -40 | -26 | -31 | -16
| M | Retail Buildings | -63 | -66 | -58 | -76 | -37 | -42 | -81 | -62 | -43 | -61 | -62 | -64 | -59 | -67 | -66 | -74 | -80 | -55 | -42
| E | Education Buildings | 15 | 13 | 21 | 14 | 18 | 12 | 1 | 20 | 25 | 8 | 30 | 14 | 8 | 19 | 10 | -5 | -1 | 13 | 8
| S-1, S-2 | Warehouse | -69 | -67 | -83 | -82 | -79 | -83 | -107 | -89 | -80 | -43 | -46 | -37 | -30 | -3 | -32 | -18 | -18 | -5 | 41
| Other | Other | -19 | -19 | -15 | -16 | -8 | -12 | -26 | -10 | 4 | -25 | -4 | -7 | -28 | -5 | -2 | -39 | -27 | -23 | -9
|  | Minimum Carryover Credit | 5 |  |  |  | Roundoff Carryover Credit adder | 2
| Carryover surplus load management points allowed | [5 empty] | Table C406.1.1(2)
% of Req'd | Use group and building type |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
16.7% | R-2, R-4, I-1 | Multi-family/Dormitory | 19 | 25 | 27 | 29 | 33 | 20 | 15 | 37 | 36 | 5 | 37 | 34 | 5 | 8 | 36 | 5 | 5 | 5 | 5
19.89% | I-2 | Healthcare | 17 | 13 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 7 | 16 | 20 | 15 | 21 | 20 | 43
10% | R-1 | Hotel/Motel | 9 | 5 | 9 | 5 | 22 | 7 | 13 | 23 | 25 | 5 | 22 | 19 | 5 | 18 | 16 | 5 | 5 | 5 | 6
12.13% | B | Office Buildings | 5 | 5 | 5 | 5 | 6 | 6 | 5 | 9 | 13 | 10 | 26 | 20 | 9 | 25 | 34 | 5 | 9 | 9 | 32
11.86% | A-2 | Restaurant Buildings | 31 | 28 | 25 | 26 | 23 | 16 | 5 | 8 | 16 | 5 | 8 | 7 | 5 | 5 | 9 | 5 | 5 | 5 | 5
4.553% | M | Retail Buildings | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
16.94% | E | Education Buildings | 17 | 15 | 23 | 16 | 20 | 14 | 5 | 22 | 27 | 10 | 32 | 16 | 10 | 21 | 12 | 5 | 5 | 15 | 10
6.578% | S-1, S-2 | Warehouse | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 43
9.922% | Other | Other | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
12.06%
3.981% | 33% | of recent new construction has fossil fuels, so impact on energy credits is | [21 empty] | PV Credits for 0.1 W/sf
0.3583% | 9% | Maximum energy credits showing small % of total building energy use
PV W/sf required to meet carry-over need with no LM carry over
| Use group and building type |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8 |  |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
| R-2, R-4, I-1 | Multi-family/Dormitory | 0.18889 | 0.15333 | 0.22727 | 0.15882 | 0.17222 | 0.09 | 0.068421 | 0.16667 | 0.26154 | 0 | 0.26923 | 0.35556 | 0 | 0.054545 | 0.34 | 0 | 0 | 0 | 0 | 1.5 | Multi-family/Dormitory | 9 | 15 | 11 | 17 | 18 | 20 | 19 | 21 | 13 | 10 | 13 | 9 | 9 | 11 | 10 | 9 | 10 | 9 | 7
| I-2 | Healthcare | 0.25 | 0.18333 | 0.13333 | 0.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.083333 | 0.2 | 0.25714 | 0.21667 | 0.27143 | 0.36 | 1.025 |  | Healthcare | 6 | 6 | 6 | 6 | 6 | 8 | 7 | 9 | 8 | 6 | 8 | 6 | 6 | 7 | 7 | 6 | 7 | 5 | 4
| R-1 | Hotel/Motel | 0.077778 | 0 | 0.058333 | 0 | 0.18182 | 0.045455 | 0.11 | 0.175 | 0.17692 | 0.022222 | 0.16667 | 0.2125 | 0 | 0.14545 | 0.15556 | 0 | 0.011111 | 0 | 0.08 |  | Hotel/Motel | 9 | 8 | 12 | 9 | 11 | 11 | 10 | 12 | 13 | 9 | 12 | 8 | 9 | 11 | 9 | 8 | 9 | 7 | 5
| B | Office Buildings | 0.014286 | 0 | 0 | 0.013333 | 0.023529 | 0.021053 | 0 | 0.031818 | 0.045833 | 0.047059 | 0.10909 | 0.1125 | 0.05 | 0.12778 | 0.17778 | 0 | 0.041176 | 0.05 | 0.27273 |  | Office | 14 | 14 | 17 | 15 | 17 | 19 | 18 | 22 | 24 | 17 | 22 | 16 | 14 | 18 | 18 | 14 | 17 | 14 | 11
| A-2 | Restaurant Buildings | 1.45 | 1.3 | 1.15 | 1.2 | 1.05 | 0.7 | 0 | 0.2 | 0.35 | 0 | 0.2 | 0.25 | 0 | 0 | 0.35 | 0 | 0 | 0 | 0 |  | Restaurant | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 4 | 2 | 3 | 2 | 2 | 3 | 2 | 2 | 2 | 2 | 1
| M | Retail Buildings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Retail | 8 | 8 | 12 | 9 | 11 | 12 | 12 | 17 | 17 | 11 | 13 | 9 | 10 | 11 | 10 | 9 | 10 | 9 | 6
| E | Education Buildings | 0.15 | 0.11818 | 0.16154 | 0.11667 | 0.13846 | 0.075 | 0.0066667 | 0.095238 | 0.11364 | 0.053333 | 0.15789 | 0.093333 | 0.057143 | 0.11176 | 0.0625 | 0 | 0 | 0.10833 | 0.08 |  | School/Education | 10 | 11 | 13 | 12 | 13 | 16 | 15 | 21 | 22 | 15 | 19 | 15 | 14 | 17 | 16 | 13 | 16 | 12 | 10
| S-1, S-2 | Warehouse | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25625 |  | Warehouse | 38 | 37 | 55 | 45 | 53 | 53 | 49 | 58 | 66 | 36 | 56 | 38 | 29 | 41 | 36 | 24 | 32 | 23 | 16
Load Management Points available for carryover net of revised (lowered) requirement (CED1-188)
Surplus LM (G01,G02,G06) after meet LM/PV requirements with only LM
| Building Occupancy Group |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | SA | SB | SC | 6A | 6B | 7 | 8
| R-2, R-4, and 1-1 | Multi-family/Dormitory | 41 | 28 | 18 | 19 | 6 | 16 | 12 | 6 | 24 | 16 | 26 | 27 | 21 | 19 | 23 | 10 | 12 | 15 | 20
| I-2 | Healthcare | 2 | 3 | 2 | 2 | 0 | 9 | 0 | -4 | 1 | 3 | 6 | 4 | 4 | 4 | 3 | 4 | 1 | 3 | 3
| R-1 | Hotel/Motel | 7 | 9 | 4 | 8 | 6 | 7 | 9 | 6 | 5 | 11 | 6 | 15 | 10 | 7 | 13 | 10 | 10 | 11 | 14
| B | Office Buildings | -23 | -13 | -18 | -15 | -19 | -29 | -21 | -25 | -33 | -15 | -29 | -14 | -12 | -19 | -16 | -14 | -18 | -12 | -14
| A-2 | Restaurant Buildings | 41 | 35 | 48 | 38 | 42 | 38 | 39 | 33 | 34 | 32 | 28 | 29 | 31 | 25 | 24 | 27 | 26 | 24 | 12
| M | Retail Buildings | -13 | -13 | -4 | 0 | -3 | -14 | -5 | -9 | -16 | 5 | -7 | 10 | 1 | 1 | 11 | 0 | 1 | 4 | -6
| E | Education Buildings | 3 | 5 | 12 | 4 | 5 | 5 | 3 | -9 | -16 | 0 | 0 | 2 | -1 | 4 | -12 | -1 | 2 | -1 | -5
| S-1 and S-2 | Warehouse | -55 | -15 | -18 | -22 | -26 | -16 | -21 | -27 | -28 | -33 | -42 | -37 | -39 | -51 | -53 | -32 | -54 | -34 | -27
| All Other |  | 9 | 7 | 2 | 4 | -1 | -2 | -2 | -7 | -11 | 3 | -4 | 4 | 3 | -1 | -2 | 1 | -1 | 3 | -1
Restaurant Building example
|  | Carryover Needed | 31 | 28 | 25 | 26 | 23 | 16 | 5 | 8 | 16 | 5 | 8 | 7 | 5 | 5 | 9 | 5 | 5 | 5 | 5
|  | Surplus LM Points (No PV) | 41 | 35 | 48 | 38 | 42 | 38 | 39 | 33 | 34 | 32 | 28 | 29 | 31 | 25 | 24 | 27 | 26 | 24 | 12
| 0.15 | LM Credits applyable | 6.15 | 5.25 | 7.2 | 5.7 | 6.3 | 5.7 | 5 | 4.95 | 5.1 | 4.8 | 4.2 | 4.35 | 4.65 | 3.75 | 3.6 | 4.05 | 3.9 | 3.6 | 1.8
| 0.3 |  | 12.3 | 10.5 | 14.4 | 11.4 | 12.6 | 11.4 | 5 | 8 | 10.2 | 5 | 8 | 7 | 5 | 5 | 7.2 | 5 | 5 | 5 | 3.6
| 0.5 |  | 20.5 | 17.5 | 24 | 19 | 21 | 16 | 5 | 8 | 16 | 5 | 8 | 7 | 5 | 5 | 9 | 5 | 5 | 5 | 5
| 0.7 | Agreed to adjustment | 28.7 | 24.5 | 25 | 26 | 23 | 16 | 5 | 8 | 16 | 5 | 8 | 7 | 5 | 5 | 9 | 5 | 5 | 5 | 5
| 1 |  | 31 | 28 | 25 | 26 | 23 | 16 | 5 | 8 | 16 | 5 | 8 | 7 | 5 | 5 | 9 | 5 | 5 | 5 | 5
|  |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
|  | Renewable Credits per 0.1 W/sf | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 4 | 2 | 3 | 2 | 2 | 3 | 2 | 2 | 2 | 2 | 1
| 0.15 | Renewable needed W/sf | 1.2425 | 1.1375 | 0.89 | 1.015 | 0.835 | 0.515 | 0 | 0.10167 | 0.2725 | 0.01 | 0.12667 | 0.1325 | 0.0175 | 0.041667 | 0.27 | 0.0475 | 0.055 | 0.07 | 0.32 | 1.5
| 0.3 |  | 0.935 | 0.875 | 0.53 | 0.73 | 0.52 | 0.23 | 0 | 0 | 0.145 | 0 | 0 | 0 | 0 | 0 | 0.09 | 0 | 0 | 0 | 0.14
| 0.5 |  | 0.525 | 0.525 | 0.05 | 0.35 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 0.7 | Agreed to adjustment | 0.115 | 0.175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Health building example
|  | Carryover Needed | 17 | 13 | 10 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 7 | 16 | 20 | 15 | 21 | 20 | 43
|  | Surplus LM Points (No PV) | 2 | 3 | 2 | 2 | 0 | 9 | 0 | -4 | 1 | 3 | 6 | 4 | 4 | 4 | 3 | 4 | 1 | 3 | 3
| 0.15 | LM Credits applyable | 0.3 | 0.45 | 0.3 | 0.3 | 0 | 1.35 | 0 | 0 | 0.15 | 0.45 | 0.9 | 0.6 | 0.6 | 0.6 | 0.45 | 0.6 | 0.15 | 0.45 | 0.45
| 0.3 |  | 0.6 | 0.9 | 0.6 | 0.6 | 0 | 2.7 | 0 | 0 | 0.3 | 0.9 | 1.8 | 1.2 | 1.2 | 1.2 | 0.9 | 1.2 | 0.3 | 0.9 | 0.9
| 0.5 |  | 1 | 1.5 | 1 | 1 | 0 | 4.5 | 0 | 0 | 0.5 | 1.5 | 3 | 2 | 2 | 2 | 1.5 | 2 | 0.5 | 1.5 | 1.5
| 0.7 | Agreed to adjustment | 1.4 | 2.1 | 1.4 | 1.4 | 0 | 5 | 0 | 0 | 0.7 | 2.1 | 4.2 | 2.8 | 2.8 | 2.8 | 2.1 | 2.8 | 0.7 | 2.1 | 2.1
| 1 |  | 2 | 3 | 2 | 2 | 0 | 5 | 0 | 0 | 1 | 3 | 5 | 4 | 4 | 4 | 3 | 4 | 1 | 3 | 3
|  |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
|  | Renewable Credits per 0.1 W/sf | 6 | 6 | 6 | 6 | 6 | 8 | 7 | 9 | 8 | 6 | 8 | 6 | 6 | 7 | 7 | 6 | 7 | 5 | 4
| 0.15 | Renewable needed W/sf | 0.27833 | 0.20917 | 0.16167 | 0.078333 | 0.083333 | 0.045625 | 0.071429 | 0.055556 | 0.060625 | 0.075833 | 0.05125 | 0.073333 | 0.10667 | 0.22 | 0.27929 | 0.24 | 0.29786 | 0.391 | 1.0637 | 1.5
| 0.3 |  | 0.27333 | 0.20167 | 0.15667 | 0.073333 | 0.083333 | 0.02875 | 0.071429 | 0.055556 | 0.05875 | 0.068333 | 0.04 | 0.063333 | 0.096667 | 0.21143 | 0.27286 | 0.23 | 0.29571 | 0.382 | 1.0525
| 0.5 |  | 0.26667 | 0.19167 | 0.15 | 0.066667 | 0.083333 | 0.00625 | 0.071429 | 0.055556 | 0.05625 | 0.058333 | 0.025 | 0.05 | 0.083333 | 0.2 | 0.26429 | 0.21667 | 0.29286 | 0.37 | 1.0375
| 0.7 | Agreed to adjustment | 0.26 | 0.18167 | 0.14333 | 0.06 | 0.083333 | 0 | 0.071429 | 0.055556 | 0.05375 | 0.048333 | 0.01 | 0.036667 | 0.07 | 0.18857 | 0.25571 | 0.20333 | 0.29 | 0.358 | 1.0225
| 1 |  | 0.25 | 0.16667 | 0.13333 | 0.05 | 0.083333 | 0 | 0.071429 | 0.055556 | 0.05 | 0.033333 | 0 | 0.016667 | 0.05 | 0.17143 | 0.24286 | 0.18333 | 0.28571 | 0.34 | 1
Education Building example
|  | Carryover Needed | 17 | 15 | 23 | 16 | 20 | 14 | 5 | 22 | 27 | 10 | 32 | 16 | 10 | 21 | 12 | 5 | 5 | 15 | 10
|  | Surplus LM Points (No PV) | 3 | 5 | 12 | 4 | 5 | 5 | 3 | -9 | -16 | 0 | 0 | 2 | -1 | 4 | -12 | -1 | 2 | -1 | -5
| 0.15 | LM Credits applyable | 0.45 | 0.75 | 1.8 | 0.6 | 0.75 | 0.75 | 0.45 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0.6 | 0 | 0 | 0.3 | 0 | 0
| 0.3 |  | 0.9 | 1.5 | 3.6 | 1.2 | 1.5 | 1.5 | 0.9 | 0 | 0 | 0 | 0 | 0.6 | 0 | 1.2 | 0 | 0 | 0.6 | 0 | 0
| 0.5 |  | 1.5 | 2.5 | 6 | 2 | 2.5 | 2.5 | 1.5 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 0 | 1 | 0 | 0
| 0.7 | Agreed to adjustment | 2.1 | 3.5 | 8.4 | 2.8 | 3.5 | 3.5 | 2.1 | 0 | 0 | 0 | 0 | 1.4 | 0 | 2.8 | 0 | 0 | 1.4 | 0 | 0
| 1 |  | 3 | 5 | 12 | 4 | 5 | 5 | 3 | 0 | 0 | 0 | 0 | 2 | 0 | 4 | 0 | 0 | 2 | 0 | 0
|  |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
|  | Renewable Credits per 0.1 W/sf | 10 | 11 | 13 | 12 | 13 | 16 | 15 | 21 | 22 | 15 | 19 | 15 | 14 | 17 | 16 | 13 | 16 | 12 | 10
| 0.15 | Renewable needed W/sf | 0.1655 | 0.12955 | 0.16308 | 0.12833 | 0.14808 | 0.082812 | 0.030333 | 0.10476 | 0.12273 | 0.066667 | 0.16842 | 0.10467 | 0.071429 | 0.12 | 0.075 | 0.038462 | 0.029375 | 0.125 | 0.1 | 1.5
| 0.3 |  | 0.161 | 0.12273 | 0.14923 | 0.12333 | 0.14231 | 0.078125 | 0.027333 | 0.10476 | 0.12273 | 0.066667 | 0.16842 | 0.10267 | 0.071429 | 0.11647 | 0.075 | 0.038462 | 0.0275 | 0.125 | 0.1
| 0.5 |  | 0.155 | 0.11364 | 0.13077 | 0.11667 | 0.13462 | 0.071875 | 0.023333 | 0.10476 | 0.12273 | 0.066667 | 0.16842 | 0.1 | 0.071429 | 0.11176 | 0.075 | 0.038462 | 0.025 | 0.125 | 0.1
| 0.7 | Agreed to adjustment | 0.149 | 0.10455 | 0.11231 | 0.11 | 0.12692 | 0.065625 | 0.019333 | 0.10476 | 0.12273 | 0.066667 | 0.16842 | 0.097333 | 0.071429 | 0.10706 | 0.075 | 0.038462 | 0.0225 | 0.125 | 0.1
| 1 |  | 0.14 | 0.090909 | 0.084615 | 0.1 | 0.11538 | 0.05625 | 0.013333 | 0.10476 | 0.12273 | 0.066667 | 0.16842 | 0.093333 | 0.071429 | 0.1 | 0.075 | 0.038462 | 0.01875 | 0.125 | 0.1

## Carry-overForCD-1.25
Carryover analysis for Appendix CF "Advanced Energy Credit Package" requirements
Changes for advanced package from base package highlighted
CF/CD: | Alternate high efficiency measure selections without regulated equipment above minimum (Appendix CD/CF)
| Selections w/o improved equip. efficiency |  | R-2/4, I-1 | I-2 | R-1 | B | A-2 | M | E | S-1/2
| ID | Measure | MF | Health | Htl | Ofc | Rest | Rtl | Sch | Whse | Other
| E03 | Envelope Leakage Reduction | Y | Y | Y | Y | Y | Y | Y | Y | Y
| E04 | Add R-10 Roof Insulation | Y | Y | Y | Y | Y | Y | Y | Y | Y
| E05 | Add R-5ci Wall Insulation | Y | Y | Y | Y | Y | Y | Y | Y | Y
| E06 | Improve Fenestration | Y | Y | Y | Y | Y | Y | Y | Y | Y
| H04 | Residential HVAC control. | Y
| W01 | SHW preheat recovery |  | 30% | 30% | [6 empty] | of SHW load
| W02 | Heat pump water heater |  |  | 30% |  | 60% |  |  |  |  | of SHW load
| W04 | SHW pipe insulation |  | Y | Y |  | Y | Y | Y |  | Y
| W05 | Point of use water heaters |  |  |  | Y |  |  | Y
| W06 | Thermostatic balancing valves |  | Y
| W07 | SHW heat trace system |  |  | Y
| W09 | SHW flow reduction | Y |  | Y
| L02 | Lighting high end trim |  | Y |  | Y |  |  | Y
| L03 | Increase occupancy sensor
| L04 | Increase daylight area |  |  |  | 10% |  | 20% |  | 20% |  | of floor area
| L05 | Residential light control | Y
| L06 | Lighting power reduction | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | of LPD
| Q01 | Efficient Elevator |  | Y | Y | Y
| Q02 | Efficient Commercial Kitchen Equipment |  |  |  |  | Y
| Q04 | Fault detection |  | Y | Y | Y | Y | Y | Y | Y | Y
Energy Efficiency Credits Achieved by reasonable package without equipment efficiency improvement
| Use group and building type |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
| R-2, R-4, I-1 | Multi-family/Dormitory | 81 | 76 | 76 | 89 | 89 | 111 | 107 | 87 | 101 | 129 | 100 | 103 | 141 | 129 | 101 | 157 | 152 | 136 | 140
| I-2 | Healthcare | 50 | 52 | 49 | 53 | 54 | 59 | 64 | 56 | 59 | 62 | 55 | 60 | 60 | 51 | 48 | 56 | 52 | 57 | 39
| R-1 | Hotel/Motel | 88 | 94 | 92 | 103 | 85 | 102 | 105 | 99 | 103 | 120 | 105 | 115 | 135 | 113 | 121 | 146 | 130 | 139 | 124
| B | Office Buildings | 91 | 93 | 96 | 97 | 95 | 94 | 103 | 89 | 91 | 97 | 84 | 93 | 100 | 87 | 84 | 112 | 104 | 104 | 77
| A-2 | Restaurant Buildings | 76 | 79 | 85 | 84 | 92 | 99 | 112 | 104 | 109 | 119 | 105 | 112 | 128 | 110 | 110 | 130 | 126 | 116 | 92
| M | Retail Buildings | 183 | 184 | 182 | 194 | 158 | 168 | 181 | 173 | 173 | 181 | 161 | 161 | 177 | 160 | 141 | 186 | 180 | 167 | 129
| E | Education Buildings | 69 | 73 | 62 | 73 | 69 | 74 | 88 | 73 | 64 | 84 | 69 | 79 | 88 | 82 | 91 | 102 | 101 | 82 | 79
| S-1, S-2 | Warehouse | 160 | 157 | 174 | 172 | 166 | 168 | 173 | 170 | 173 | 170 | 148 | 149 | 165 | 126 | 140 | 153 | 151 | 140 | 94
| Other | Other | 65 | 65 | 61 | 64 | 56 | 61 | 71 | 58 | 50 | 77 | 56 | 59 | 83 | 59 | 56 | 93 | 82 | 77 | 60
Appendis CD: Requirements are 1.4 of final table; based here on PD2-requirements, with 1.25 multiplied included.
Min of |  |  |  | 1.75
5 |  | Building Use Type | Climate Zone
% of Req'd |  |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8 | Avg
3.523% | R-2, R-4, I-1 | Multi-family/Dormitory | 113.75 | 115.5 | 117.25 | 134.75 | 140 | 150.5 | 140 | 141.75 | 157.5 | 150.5 | 157.5 | 157.5 | 150.5 | 157.5 | 157.5 | 122.5 | 155.75 | 140 | 136.5 | 141.9342
7.133% | I-2 | Healthcare | 75.25 | 73.5 | 66.5 | 64.75 | 63 | 66.5 | 56 | 56 | 52.5 | 63 | 63 | 61.25 | 75.25 | 75.25 | 77 | 80.5 | 82.25 | 87.5 | 92.75 | 70.0921
3.636% | R-1 | Hotel/Motel | 110.25 | 108.5 | 115.5 | 113.75 | 122.5 | 124.25 | 134.75 | 140 | 147 | 141.75 | 145.25 | 154 | 148.75 | 150.5 | 157.5 | 145.25 | 152.25 | 152.25 | 148.75 | 137.5132
4.15% | B | Office Buildings | 108.5 | 108.5 | 112 | 115.5 | 115.5 | 113.75 | 112 | 112 | 119 | 122.5 | 126 | 129.5 | 124.25 | 127.75 | 134.75 | 124.25 | 129.5 | 129.5 | 124.25 | 120.4737
4.076% | A-2 | Restaurant Buildings | 122.5 | 122.5 | 126 | 126 | 131.25 | 131.25 | 122.5 | 127.75 | 143.5 | 120.75 | 129.5 | 136.5 | 117.25 | 126 | 136.5 | 105 | 117.25 | 99.75 | 89.25 | 122.6842
3.903% | M | Retail Buildings | 140 | 138.25 | 145.25 | 138.25 | 141.75 | 147 | 117.25 | 129.5 | 152.25 | 140 | 115.5 | 113.75 | 138.25 | 108.5 | 87.5 | 131.25 | 117.25 | 131.25 | 101.5 | 128.1184
4.676% | E | School/Education Buildings | 98 | 99.75 | 96.25 | 101.5 | 101.5 | 99.75 | 103.25 | 108.5 | 103.25 | 106.75 | 115.5 | 108.5 | 112 | 117.25 | 117.25 | 113.75 | 117.25 | 110.25 | 101.5 | 106.9342
4.027% | S-1, S-2 | Warehouse and Semiheated | 106.75 | 105 | 106.75 | 105 | 101.5 | 99.75 | 77 | 94.5 | 108.5 | 148.75 | 119 | 131.25 | 157.5 | 143.5 | 126 | 157.5 | 155.75 | 157.5 | 157.5 | 124.1579
8.416% | Other | Other | 54.25 | 54.25 | 54.25 | 56 | 56 | 57.75 | 52.5 | 56 | 63 | 61.25 | 61.25 | 61.25 | 64.75 | 63 | 63 | 63 | 64.75 | 63 | 59.5 | 59.4079
4.838%
Carryover surplus load management points needed with no increases in regulated equipment efficiency
| Use group and building type |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
| R-2, R-4, I-1 | Multi-family/Dormitory | 33 | 40 | 42 | 46 | 51 | 40 | 33 | 55 | 57 | 22 | 58 | 55 | 10 | 29 | 57 | -35 | 4 | 4 | -4
| I-2 | Healthcare | 26 | 22 | 18 | 12 | 9 | 8 | -8 | 0 | -7 | 1 | 8 | 2 | 16 | 25 | 29 | 25 | 31 | 31 | 54
| R-1 | Hotel/Motel | 23 | 15 | 24 | 11 | 38 | 23 | 30 | 41 | 44 | 22 | 41 | 39 | 14 | 38 | 37 | -1 | 23 | 14 | 25
| B | Office Buildings | 18 | 16 | 16 | 19 | 21 | 20 | 9 | 23 | 28 | 26 | 42 | 37 | 25 | 41 | 51 | 13 | 26 | 26 | 48
| A-2 | Restaurant Buildings | 47 | 44 | 41 | 42 | 40 | 33 | 11 | 24 | 35 | 2 | 25 | 25 | -11 | 16 | 27 | -25 | -9 | -17 | -3
| M | Retail Buildings | -43 | -46 | -37 | -56 | -17 | -21 | -64 | -44 | -21 | -41 | -46 | -48 | -39 | -52 | -54 | -55 | -63 | -36 | -28
| E | Education Buildings | 29 | 27 | 35 | 29 | 33 | 26 | 16 | 36 | 40 | 23 | 47 | 30 | 24 | 36 | 27 | 12 | 17 | 29 | 23
| S-1, S-2 | Warehouse | -54 | -52 | -68 | -67 | -65 | -69 | -96 | -76 | -65 | -22 | -29 | -18 | -8 | 18 | -14 | 5 | 5 | 18 | 64
| Other | Other | -11 | -11 | -7 | -8 | 0 | -4 | -19 | -2 | 13 | -16 | 6 | 3 | -19 | 4 | 7 | -30 | -18 | -14 | -1
|  | Minimum Carryover Credit | 5 |  |  |  | Roundoff Carryover Credit adder | 2
| Carryover surplus load management points allowed | [5 empty] | Table C406.1.1(2)
% of Req'd | Use group and building type |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
25.22% | R-2, R-4, I-1 | Multi-family/Dormitory | 35 | 42 | 44 | 48 | 53 | 42 | 35 | 57 | 59 | 24 | 60 | 57 | 12 | 31 | 59 | 5 | 6 | 6 | 5
27.56% | I-2 | Healthcare | 28 | 24 | 20 | 14 | 11 | 10 | 5 | 5 | 5 | 5 | 10 | 5 | 18 | 27 | 31 | 27 | 33 | 33 | 56
20.78% | R-1 | Hotel/Motel | 25 | 17 | 26 | 13 | 40 | 25 | 32 | 43 | 46 | 24 | 43 | 41 | 16 | 40 | 39 | 5 | 25 | 16 | 27
23.72% | B | Office Buildings | 20 | 18 | 18 | 21 | 23 | 22 | 11 | 25 | 30 | 28 | 44 | 39 | 27 | 43 | 53 | 15 | 28 | 28 | 50
19.99% | A-2 | Restaurant Buildings | 49 | 46 | 43 | 44 | 42 | 35 | 13 | 26 | 37 | 5 | 27 | 27 | 5 | 18 | 29 | 5 | 5 | 5 | 5
3.903% | M | Retail Buildings | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
28.4% | E | Education Buildings | 31 | 29 | 37 | 31 | 35 | 28 | 18 | 38 | 42 | 25 | 49 | 32 | 26 | 38 | 29 | 14 | 19 | 31 | 25
8.054% | S-1, S-2 | Warehouse | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 20 | 5 | 7 | 7 | 20 | 66
10.01% | Other | Other | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 15 | 5 | 8 | 5 | 5 | 6 | 9 | 5 | 5 | 5 | 5
18.63%
6.147% | 33% | of recent new construction has fossil fuels, so impact on energy credits is | [21 empty] | PV Credits for 0.1 W/sf
0.5532% | 9% | Maximum energy credits showing small % of total building energy use
PV W/sf required to meet carry-over need with no LM carry over
| Use group and building type |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8 |  |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
| R-2, R-4, I-1 | Multi-family/Dormitory | 0.36667 | 0.26667 | 0.38182 | 0.27059 | 0.28333 | 0.2 | 0.17368 | 0.2619 | 0.43846 | 0.22 | 0.44615 | 0.61111 | 0.11111 | 0.26364 | 0.57 | 0 | 0.04 | 0.044444 | 0 | 1.5 | Multi-family/Dormitory | 9 | 15 | 11 | 17 | 18 | 20 | 19 | 21 | 13 | 10 | 13 | 9 | 9 | 11 | 10 | 9 | 10 | 9 | 7
| I-2 | Healthcare | 0.43333 | 0.36667 | 0.3 | 0.2 | 0.15 | 0.1 | 0 | 0 | 0 | 0.016667 | 0.1 | 0.033333 | 0.26667 | 0.35714 | 0.41429 | 0.41667 | 0.44286 | 0.62 | 1.35 |  | Healthcare | 6 | 6 | 6 | 6 | 6 | 8 | 7 | 9 | 8 | 6 | 8 | 6 | 6 | 7 | 7 | 6 | 7 | 5 | 4
| R-1 | Hotel/Motel | 0.25556 | 0.1875 | 0.2 | 0.12222 | 0.34545 | 0.20909 | 0.3 | 0.34167 | 0.33846 | 0.24444 | 0.34167 | 0.4875 | 0.15556 | 0.34545 | 0.41111 | 0 | 0.25556 | 0.2 | 0.5 |  | Hotel/Motel | 9 | 8 | 12 | 9 | 11 | 11 | 10 | 12 | 13 | 9 | 12 | 8 | 9 | 11 | 9 | 8 | 9 | 7 | 5
| B | Office Buildings | 0.12857 | 0.11429 | 0.094118 | 0.12667 | 0.12353 | 0.10526 | 0.05 | 0.10455 | 0.11667 | 0.15294 | 0.19091 | 0.23125 | 0.17857 | 0.22778 | 0.28333 | 0.092857 | 0.15294 | 0.18571 | 0.43636 |  | Office | 14 | 14 | 17 | 15 | 17 | 19 | 18 | 22 | 24 | 17 | 22 | 16 | 14 | 18 | 18 | 14 | 17 | 14 | 11
| A-2 | Restaurant Buildings | 2.35 | 2.2 | 2.05 | 2.1 | 2 | 1.65 | 0.55 | 0.8 | 0.875 | 0.1 | 0.83333 | 1.25 | 0 | 0.53333 | 1.35 | 0 | 0 | 0 | 0 |  | Restaurant | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 4 | 2 | 3 | 2 | 2 | 3 | 2 | 2 | 2 | 2 | 1
| M | Retail Buildings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Retail | 8 | 8 | 12 | 9 | 11 | 12 | 12 | 17 | 17 | 11 | 13 | 9 | 10 | 11 | 10 | 9 | 10 | 9 | 6
| E | Education Buildings | 0.29 | 0.24545 | 0.26923 | 0.24167 | 0.25385 | 0.1625 | 0.10667 | 0.17143 | 0.18182 | 0.15333 | 0.24737 | 0.2 | 0.17143 | 0.21176 | 0.16875 | 0.092308 | 0.10625 | 0.24167 | 0.23 |  | School/Education | 10 | 11 | 13 | 12 | 13 | 16 | 15 | 21 | 22 | 15 | 19 | 15 | 14 | 17 | 16 | 13 | 16 | 12 | 10
| S-1, S-2 | Warehouse | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.043902 | 0 | 0.020833 | 0.015625 | 0.078261 | 0.4 |  | Warehouse | 38 | 37 | 55 | 45 | 53 | 53 | 49 | 58 | 66 | 36 | 56 | 38 | 29 | 41 | 36 | 24 | 32 | 23 | 16
Load Management Points available for carryover net of revised (lowered) requirement (CED1-188)
Surplus LM (G01,G02,G06) after meet LM/PV requirements with only LM
| Building Occupancy Group |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | SA | SB | SC | 6A | 6B | 7 | 8
| R-2, R-4, and 1-1 | Multi-family/Dormitory | 41 | 28 | 18 | 19 | 6 | 16 | 12 | 6 | 24 | 16 | 26 | 27 | 21 | 19 | 23 | 10 | 12 | 15 | 20
| I-2 | Healthcare | 2 | 3 | 2 | 2 | 0 | 9 | 0 | -4 | 1 | 3 | 6 | 4 | 4 | 4 | 3 | 4 | 1 | 3 | 3
| R-1 | Hotel/Motel | 7 | 9 | 4 | 8 | 6 | 7 | 9 | 6 | 5 | 11 | 6 | 15 | 10 | 7 | 13 | 10 | 10 | 11 | 14
| B | Office Buildings | -23 | -13 | -18 | -15 | -19 | -29 | -21 | -25 | -33 | -15 | -29 | -14 | -12 | -19 | -16 | -14 | -18 | -12 | -14
| A-2 | Restaurant Buildings | 41 | 35 | 48 | 38 | 42 | 38 | 39 | 33 | 34 | 32 | 28 | 29 | 31 | 25 | 24 | 27 | 26 | 24 | 12
| M | Retail Buildings | -13 | -13 | -4 | 0 | -3 | -14 | -5 | -9 | -16 | 5 | -7 | 10 | 1 | 1 | 11 | 0 | 1 | 4 | -6
| E | Education Buildings | 3 | 5 | 12 | 4 | 5 | 5 | 3 | -9 | -16 | 0 | 0 | 2 | -1 | 4 | -12 | -1 | 2 | -1 | -5
| S-1 and S-2 | Warehouse | -55 | -15 | -18 | -22 | -26 | -16 | -21 | -27 | -28 | -33 | -42 | -37 | -39 | -51 | -53 | -32 | -54 | -34 | -27
| All Other |  | 9 | 7 | 2 | 4 | -1 | -2 | -2 | -7 | -11 | 3 | -4 | 4 | 3 | -1 | -2 | 1 | -1 | 3 | -1
Restaurant Building example
|  | Carryover Needed | 49 | 46 | 43 | 44 | 42 | 35 | 13 | 26 | 37 | 5 | 27 | 27 | 5 | 18 | 29 | 5 | 5 | 5 | 5
|  | Surplus LM Points (No PV) | 41 | 35 | 48 | 38 | 42 | 38 | 39 | 33 | 34 | 32 | 28 | 29 | 31 | 25 | 24 | 27 | 26 | 24 | 12
| 0.15 | LM Credits applyable | 6.15 | 5.25 | 7.2 | 5.7 | 6.3 | 5.7 | 5.85 | 4.95 | 5.1 | 4.8 | 4.2 | 4.35 | 4.65 | 3.75 | 3.6 | 4.05 | 3.9 | 3.6 | 1.8
| 0.3 |  | 12.3 | 10.5 | 14.4 | 11.4 | 12.6 | 11.4 | 11.7 | 9.9 | 10.2 | 5 | 8.4 | 8.7 | 5 | 7.5 | 7.2 | 5 | 5 | 5 | 3.6
| 0.5 |  | 20.5 | 17.5 | 24 | 19 | 21 | 19 | 13 | 16.5 | 17 | 5 | 14 | 14.5 | 5 | 12.5 | 12 | 5 | 5 | 5 | 5
| 0.7 | Agreed to adjustment | 28.7 | 24.5 | 33.6 | 26.6 | 29.4 | 26.6 | 13 | 23.1 | 23.8 | 5 | 19.6 | 20.3 | 5 | 17.5 | 16.8 | 5 | 5 | 5 | 5
| 1 |  | 41 | 35 | 43 | 38 | 42 | 35 | 13 | 26 | 34 | 5 | 27 | 27 | 5 | 18 | 24 | 5 | 5 | 5 | 5
|  |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
|  | Renewable Credits per 0.1 W/sf | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 4 | 2 | 3 | 2 | 2 | 3 | 2 | 2 | 2 | 2 | 1
| 0.15 | Renewable needed W/sf | 2.1425 | 2.0375 | 1.79 | 1.915 | 1.785 | 1.465 | 0.3575 | 0.70167 | 0.7975 | 0.01 | 0.76 | 1.1325 | 0.0175 | 0.475 | 1.27 | 0.0475 | 0.055 | 0.07 | 0.32 | 1.5
| 0.3 |  | 1.835 | 1.775 | 1.43 | 1.63 | 1.47 | 1.18 | 0.065 | 0.53667 | 0.67 | 0 | 0.62 | 0.915 | 0 | 0.35 | 1.09 | 0 | 0 | 0 | 0.14
| 0.5 |  | 1.425 | 1.425 | 0.95 | 1.25 | 1.05 | 0.8 | 0 | 0.31667 | 0.5 | 0 | 0.43333 | 0.625 | 0 | 0.18333 | 0.85 | 0 | 0 | 0 | 0
| 0.7 | Agreed to adjustment | 1.015 | 1.075 | 0.47 | 0.87 | 0.63 | 0.42 | 0 | 0.096667 | 0.33 | 0 | 0.24667 | 0.335 | 0 | 0.016667 | 0.61 | 0 | 0 | 0 | 0
| 1 |  | 0.4 | 0.55 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0.075 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0 | 0 | 0 | 0
Health building example
|  | Carryover Needed | 28 | 24 | 20 | 14 | 11 | 10 | 5 | 5 | 5 | 5 | 10 | 5 | 18 | 27 | 31 | 27 | 33 | 33 | 56
|  | Surplus LM Points (No PV) | 2 | 3 | 2 | 2 | 0 | 9 | 0 | -4 | 1 | 3 | 6 | 4 | 4 | 4 | 3 | 4 | 1 | 3 | 3
| 0.15 | LM Credits applyable | 0.3 | 0.45 | 0.3 | 0.3 | 0 | 1.35 | 0 | 0 | 0.15 | 0.45 | 0.9 | 0.6 | 0.6 | 0.6 | 0.45 | 0.6 | 0.15 | 0.45 | 0.45
| 0.3 |  | 0.6 | 0.9 | 0.6 | 0.6 | 0 | 2.7 | 0 | 0 | 0.3 | 0.9 | 1.8 | 1.2 | 1.2 | 1.2 | 0.9 | 1.2 | 0.3 | 0.9 | 0.9
| 0.5 |  | 1 | 1.5 | 1 | 1 | 0 | 4.5 | 0 | 0 | 0.5 | 1.5 | 3 | 2 | 2 | 2 | 1.5 | 2 | 0.5 | 1.5 | 1.5
| 0.7 | Agreed to adjustment | 1.4 | 2.1 | 1.4 | 1.4 | 0 | 6.3 | 0 | 0 | 0.7 | 2.1 | 4.2 | 2.8 | 2.8 | 2.8 | 2.1 | 2.8 | 0.7 | 2.1 | 2.1
| 1 |  | 2 | 3 | 2 | 2 | 0 | 9 | 0 | 0 | 1 | 3 | 6 | 4 | 4 | 4 | 3 | 4 | 1 | 3 | 3
|  |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
|  | Renewable Credits per 0.1 W/sf | 6 | 6 | 6 | 6 | 6 | 8 | 7 | 9 | 8 | 6 | 8 | 6 | 6 | 7 | 7 | 6 | 7 | 5 | 4
| 0.15 | Renewable needed W/sf | 0.46167 | 0.3925 | 0.32833 | 0.22833 | 0.18333 | 0.10812 | 0.071429 | 0.055556 | 0.060625 | 0.075833 | 0.11375 | 0.073333 | 0.29 | 0.37714 | 0.43643 | 0.44 | 0.46929 | 0.651 | 1.3887 | 1.5
| 0.3 |  | 0.45667 | 0.385 | 0.32333 | 0.22333 | 0.18333 | 0.09125 | 0.071429 | 0.055556 | 0.05875 | 0.068333 | 0.1025 | 0.063333 | 0.28 | 0.36857 | 0.43 | 0.43 | 0.46714 | 0.642 | 1.3775
| 0.5 |  | 0.45 | 0.375 | 0.31667 | 0.21667 | 0.18333 | 0.06875 | 0.071429 | 0.055556 | 0.05625 | 0.058333 | 0.0875 | 0.05 | 0.26667 | 0.35714 | 0.42143 | 0.41667 | 0.46429 | 0.63 | 1.3625
| 0.7 | Agreed to adjustment | 0.44333 | 0.365 | 0.31 | 0.21 | 0.18333 | 0.04625 | 0.071429 | 0.055556 | 0.05375 | 0.048333 | 0.0725 | 0.036667 | 0.25333 | 0.34571 | 0.41286 | 0.40333 | 0.46143 | 0.618 | 1.3475
| 1 |  | 0.43333 | 0.35 | 0.3 | 0.2 | 0.18333 | 0.0125 | 0.071429 | 0.055556 | 0.05 | 0.033333 | 0.05 | 0.016667 | 0.23333 | 0.32857 | 0.4 | 0.38333 | 0.45714 | 0.6 | 1.325
Education Building example
|  | Carryover Needed | 31 | 29 | 37 | 31 | 35 | 28 | 18 | 38 | 42 | 25 | 49 | 32 | 26 | 38 | 29 | 14 | 19 | 31 | 25
|  | Surplus LM Points (No PV) | 3 | 5 | 12 | 4 | 5 | 5 | 3 | -9 | -16 | 0 | 0 | 2 | -1 | 4 | -12 | -1 | 2 | -1 | -5
| 0.15 | LM Credits applyable | 0.45 | 0.75 | 1.8 | 0.6 | 0.75 | 0.75 | 0.45 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0.6 | 0 | 0 | 0.3 | 0 | 0
| 0.3 |  | 0.9 | 1.5 | 3.6 | 1.2 | 1.5 | 1.5 | 0.9 | 0 | 0 | 0 | 0 | 0.6 | 0 | 1.2 | 0 | 0 | 0.6 | 0 | 0
| 0.5 |  | 1.5 | 2.5 | 6 | 2 | 2.5 | 2.5 | 1.5 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 0 | 1 | 0 | 0
| 0.7 | Agreed to adjustment | 2.1 | 3.5 | 8.4 | 2.8 | 3.5 | 3.5 | 2.1 | 0 | 0 | 0 | 0 | 1.4 | 0 | 2.8 | 0 | 0 | 1.4 | 0 | 0
| 1 |  | 3 | 5 | 12 | 4 | 5 | 5 | 3 | 0 | 0 | 0 | 0 | 2 | 0 | 4 | 0 | 0 | 2 | 0 | 0
|  |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
|  | Renewable Credits per 0.1 W/sf | 10 | 11 | 13 | 12 | 13 | 16 | 15 | 21 | 22 | 15 | 19 | 15 | 14 | 17 | 16 | 13 | 16 | 12 | 10
| 0.15 | Renewable needed W/sf | 0.3055 | 0.25682 | 0.27077 | 0.25333 | 0.26346 | 0.17031 | 0.117 | 0.18095 | 0.19091 | 0.16667 | 0.25789 | 0.21133 | 0.18571 | 0.22 | 0.18125 | 0.10769 | 0.11687 | 0.25833 | 0.25 | 1.5
| 0.3 |  | 0.301 | 0.25 | 0.25692 | 0.24833 | 0.25769 | 0.16562 | 0.114 | 0.18095 | 0.19091 | 0.16667 | 0.25789 | 0.20933 | 0.18571 | 0.21647 | 0.18125 | 0.10769 | 0.115 | 0.25833 | 0.25
| 0.5 |  | 0.295 | 0.24091 | 0.23846 | 0.24167 | 0.25 | 0.15937 | 0.11 | 0.18095 | 0.19091 | 0.16667 | 0.25789 | 0.20667 | 0.18571 | 0.21176 | 0.18125 | 0.10769 | 0.1125 | 0.25833 | 0.25
| 0.7 | Agreed to adjustment | 0.289 | 0.23182 | 0.22 | 0.235 | 0.24231 | 0.15313 | 0.106 | 0.18095 | 0.19091 | 0.16667 | 0.25789 | 0.204 | 0.18571 | 0.20706 | 0.18125 | 0.10769 | 0.11 | 0.25833 | 0.25
| 1 |  | 0.28 | 0.21818 | 0.19231 | 0.225 | 0.23077 | 0.14375 | 0.1 | 0.18095 | 0.19091 | 0.16667 | 0.25789 | 0.2 | 0.18571 | 0.2 | 0.18125 | 0.10769 | 0.10625 | 0.25833 | 0.25

## CDdeficit
Table C406.1.1(2)
Carryover surplus load management DEFICIT from points allowed in PD2, if fossil fuel space or water heating equipment used
Use group and building type |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
R-2, R-4, I-1 | Multi-family/Dormitory | 16 | 17 | 17 | 19 | 20 | 22 | 20 | 20 | 23 | 19 | 23 | 23 | 7 | 23 | 23 | 0 | 1 | 1 | 0
I-2 | Healthcare | 11 | 11 | 10 | 9 | 6 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 11 | 11 | 11 | 12 | 12 | 13 | 13
R-1 | Hotel/Motel | 16 | 12 | 17 | 8 | 18 | 18 | 19 | 20 | 21 | 19 | 21 | 22 | 11 | 22 | 23 | 0 | 20 | 11 | 21
B | Office Buildings | 15 | 13 | 13 | 16 | 17 | 16 | 6 | 16 | 17 | 18 | 18 | 19 | 18 | 18 | 19 | 10 | 19 | 19 | 18
A-2 | Restaurant Buildings | 18 | 18 | 18 | 18 | 19 | 19 | 8 | 18 | 21 | 0 | 19 | 20 | 0 | 13 | 20 | 0 | 0 | 0 | 0
M | Retail Buildings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
E | Education Buildings | 14 | 14 | 14 | 15 | 15 | 14 | 13 | 16 | 15 | 15 | 17 | 16 | 16 | 17 | 17 | 9 | 14 | 16 | 15
S-1, S-2 | Warehouse | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 2 | 2 | 15 | 23
Other | Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 3 | 0 | 0 | 1 | 4 | 0 | 0 | 0 | 0
| 105 | 6 | 6 | 6 | 6 | 6 | 6 | 5 | 5 | 5 | 4 | 6 | 5 | 5 | 7 | 6 | 4 | 6 | 6 | 5
| 69.08% | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.75 | 0.625 | 0.625 | 0.625 | 0.5 | 0.75 | 0.625 | 0.625 | 0.875 | 0.75 | 0.5 | 0.75 | 0.75 | 0.625

## Carry-overForCF
Carryover analysis for Appendix CF "Advanced Energy Credit Package" requirements
Changes for advanced package from base package highlighted
CF/CD: | Alternate high efficiency measure selections without regulated equipment above minimum (Appendix CD/CF)
| Selections w/o improved equip. efficiency |  | R-2/4, I-1 | I-2 | R-1 | B | A-2 | M | E | S-1/2
| ID | Measure | MF | Health | Htl | Ofc | Rest | Rtl | Sch | Whse | Other
| E03 | Envelope Leakage Reduction | Y | Y | Y | Y | Y | Y | Y | Y | Y
| E04 | Add R-10 Roof Insulation | Y | Y | Y | Y | Y | Y | Y | Y | Y
| E05 | Add R-5ci Wall Insulation | Y | Y | Y | Y | Y | Y | Y | Y | Y
| E06 | Improve Fenestration | Y | Y | Y | Y | Y | Y | Y | Y | Y
| H04 | Residential HVAC control. | Y
| W01 | SHW preheat recovery |  | 30% | 30% | [6 empty] | of SHW load
| W02 | Heat pump water heater |  |  | 30% |  | 60% |  |  |  |  | of SHW load
| W04 | SHW pipe insulation |  | Y | Y |  | Y | Y | Y |  | Y
| W05 | Point of use water heaters |  |  |  | Y |  |  | Y
| W06 | Thermostatic balancing valves |  | Y
| W07 | SHW heat trace system |  |  | Y
| W09 | SHW flow reduction | Y |  | Y
| L02 | Lighting high end trim |  | Y |  | Y |  |  | Y
| L03 | Increase occupancy sensor
| L04 | Increase daylight area |  |  |  | 10% |  | 20% |  | 20% |  | of floor area
| L05 | Residential light control | Y
| L06 | Lighting power reduction | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | 20% | of LPD
| Q01 | Efficient Elevator |  | Y | Y | Y
| Q02 | Efficient Commercial Kitchen Equipment |  |  |  |  | Y
| Q04 | Fault detection |  | Y | Y | Y | Y | Y | Y | Y | Y
Energy Efficiency Credits Achieved by reasonable package without equipment efficiency improvement
| Use group and building type |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
| R-2, R-4, I-1 | Multi-family/Dormitory | 81 | 76 | 76 | 89 | 89 | 111 | 107 | 87 | 101 | 129 | 100 | 103 | 141 | 129 | 101 | 157 | 152 | 136 | 140
| I-2 | Healthcare | 50 | 52 | 49 | 53 | 54 | 59 | 64 | 56 | 59 | 62 | 55 | 60 | 60 | 51 | 48 | 56 | 52 | 57 | 39
| R-1 | Hotel/Motel | 88 | 94 | 92 | 103 | 85 | 102 | 105 | 99 | 103 | 120 | 105 | 115 | 135 | 113 | 121 | 146 | 130 | 139 | 124
| B | Office Buildings | 91 | 93 | 96 | 97 | 95 | 94 | 103 | 89 | 91 | 97 | 84 | 93 | 100 | 87 | 84 | 112 | 104 | 104 | 77
| A-2 | Restaurant Buildings | 76 | 79 | 85 | 84 | 92 | 99 | 112 | 104 | 109 | 119 | 105 | 112 | 128 | 110 | 110 | 130 | 126 | 116 | 92
| M | Retail Buildings | 183 | 184 | 182 | 194 | 158 | 168 | 181 | 173 | 173 | 181 | 161 | 161 | 177 | 160 | 141 | 186 | 180 | 167 | 129
| E | Education Buildings | 69 | 73 | 62 | 73 | 69 | 74 | 88 | 73 | 64 | 84 | 69 | 79 | 88 | 82 | 91 | 102 | 101 | 82 | 79
| S-1, S-2 | Warehouse | 160 | 157 | 174 | 172 | 166 | 168 | 173 | 170 | 173 | 170 | 148 | 149 | 165 | 126 | 140 | 153 | 151 | 140 | 94
| Other | Other | 65 | 65 | 61 | 64 | 56 | 61 | 71 | 58 | 50 | 77 | 56 | 59 | 83 | 59 | 56 | 93 | 82 | 77 | 60
Requirements are from CF as proposed
Min of
5 |  | Building Use Type | Climate Zone
% of Req'd |  |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8 | Avg
2.546% | R-2, R-4, I-1 | Multi-family/Dormitory | 179 | 174 | 188 | 197 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 193 | 200 | 200 | 200 | 200 | 200 | 200 | 196.3684
5.407% | I-2 | Healthcare | 78 | 75 | 73 | 71 | 80 | 90 | 100 | 85 | 90 | 97 | 83 | 90 | 99 | 90 | 96 | 107 | 106 | 130 | 117 | 92.4737
3.709% | R-1 | Hotel/Motel | 106 | 100 | 110 | 105 | 109 | 122 | 123 | 125 | 131 | 137 | 129 | 136 | 157 | 139 | 147 | 171 | 158 | 180 | 176 | 134.7895
4.048% | B | Office Buildings | 114 | 110 | 112 | 115 | 108 | 107 | 116 | 111 | 114 | 126 | 118 | 123 | 135 | 125 | 125 | 152 | 142 | 153 | 141 | 123.5263
4.468% | A-2 | Restaurant Buildings | 83 | 81 | 82 | 82 | 86 | 86 | 108 | 91 | 97 | 126 | 99 | 111 | 147 | 117 | 113 | 160 | 143 | 163 | 151 | 111.8947
4.055% | M | Retail Buildings | 113 | 113 | 121 | 118 | 123 | 127 | 116 | 116 | 133 | 109 | 100 | 92 | 99 | 134 | 125 | 171 | 146 | 150 | 137 | 123.3158
4.535% | E | School/Education Buildings | 91 | 95 | 91 | 100 | 96 | 100 | 105 | 104 | 101 | 113 | 110 | 110 | 120 | 117 | 122 | 131 | 132 | 126 | 131 | 110.2632
3.783% | S-1, S-2 | Warehouse and Semiheated | 108 | 106 | 111 | 109 | 109 | 108 | 89 | 106 | 108 | 134 | 100 | 130 | 200 | 143 | 123 | 200 | 190 | 189 | 148 | 132.1579
7.618% | Other | Other | 54 | 53 | 55 | 56 | 57 | 60 | 61 | 60 | 63 | 68 | 60 | 65 | 73 | 68 | 69 | 84 | 79 | 84 | 78 | 65.6316
4.463%
Carryover surplus load management points needed with no increases in regulated equipment efficiency
| Use group and building type |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
| R-2, R-4, I-1 | Multi-family/Dormitory | 98 | 98 | 112 | 108 | 111 | 89 | 93 | 113 | 99 | 71 | 100 | 97 | 52 | 71 | 99 | 43 | 48 | 64 | 60
| I-2 | Healthcare | 28 | 23 | 24 | 18 | 26 | 31 | 36 | 29 | 31 | 35 | 28 | 30 | 39 | 39 | 48 | 51 | 54 | 73 | 78
| R-1 | Hotel/Motel | 18 | 6 | 18 | 2 | 24 | 20 | 18 | 26 | 28 | 17 | 24 | 21 | 22 | 26 | 26 | 25 | 28 | 41 | 52
| B | Office Buildings | 23 | 17 | 16 | 18 | 13 | 13 | 13 | 22 | 23 | 29 | 34 | 30 | 35 | 38 | 41 | 40 | 38 | 49 | 64
| A-2 | Restaurant Buildings | 7 | 2 | -3 | -2 | -6 | -13 | -4 | -13 | -12 | 7 | -6 | -1 | 19 | 7 | 3 | 30 | 17 | 47 | 59
| M | Retail Buildings | -70 | -71 | -61 | -76 | -35 | -41 | -65 | -57 | -40 | -72 | -61 | -69 | -78 | -26 | -16 | -15 | -34 | -17 | 8
| E | Education Buildings | 22 | 22 | 29 | 27 | 27 | 26 | 17 | 31 | 37 | 29 | 41 | 31 | 32 | 35 | 31 | 29 | 31 | 44 | 52
| S-1, S-2 | Warehouse | -52 | -51 | -63 | -63 | -57 | -60 | -84 | -64 | -65 | -36 | -48 | -19 | 35 | 17 | -17 | 47 | 39 | 49 | 54
| Other | Other | -11 | -12 | -6 | -8 | 1 | -1 | -10 | 2 | 13 | -9 | 4 | 6 | -10 | 9 | 13 | -9 | -3 | 7 | 18
|  | Minimum Carryover Credit | 5 |  |  |  | Roundoff Carryover Credit adder | 2
| Carryover surplus load management points allowed | [5 empty] | Table C406.1.1(2)
% of Req'd | Use group and building type |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
44.6% | R-2, R-4, I-1 | Multi-family/Dormitory | 100 | 100 | 114 | 110 | 113 | 91 | 95 | 115 | 101 | 73 | 102 | 99 | 54 | 73 | 101 | 45 | 50 | 66 | 62
43.2% | I-2 | Healthcare | 30 | 25 | 26 | 20 | 28 | 33 | 38 | 31 | 33 | 37 | 30 | 32 | 41 | 41 | 50 | 53 | 56 | 75 | 80
18.78% | R-1 | Hotel/Motel | 20 | 8 | 20 | 5 | 26 | 22 | 20 | 28 | 30 | 19 | 26 | 23 | 24 | 28 | 28 | 27 | 30 | 43 | 54
25.31% | B | Office Buildings | 25 | 19 | 18 | 20 | 15 | 15 | 15 | 24 | 25 | 31 | 36 | 32 | 37 | 40 | 43 | 42 | 40 | 51 | 66
12.42% | A-2 | Restaurant Buildings | 9 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 9 | 5 | 5 | 21 | 9 | 5 | 32 | 19 | 49 | 61
4.268% | M | Retail Buildings | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 10
30.12% | E | Education Buildings | 24 | 24 | 31 | 29 | 29 | 28 | 19 | 33 | 39 | 31 | 43 | 33 | 34 | 37 | 33 | 31 | 33 | 46 | 54
12.66% | S-1, S-2 | Warehouse | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 37 | 19 | 5 | 49 | 41 | 51 | 56
11.55% | Other | Other | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 15 | 5 | 6 | 8 | 5 | 11 | 15 | 5 | 5 | 9 | 20
22.55%
7.44% | 33% | of recent new construction has fossil fuels, so impact on energy credits is | [21 empty] | PV Credits for 0.1 W/sf
0.6696% | 9% | Maximum energy credits showing small % of total building energy use
PV W/sf required to meet carry-over need with no LM carry over
| Use group and building type |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8 |  |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
| R-2, R-4, I-1 | Multi-family/Dormitory | 1.0889 | 0.65333 | 1.0182 | 0.63529 | 0.61667 | 0.445 | 0.48947 | 0.5381 | 0.76154 | 0.71 | 0.76923 | 1.0778 | 0.57778 | 0.64545 | 0.99 | 0.47778 | 0.48 | 0.71111 | 0.85714 | 1.5 | Multi-family/Dormitory | 9 | 15 | 11 | 17 | 18 | 20 | 19 | 21 | 13 | 10 | 13 | 9 | 9 | 11 | 10 | 9 | 10 | 9 | 7
| I-2 | Healthcare | 0.46667 | 0.38333 | 0.4 | 0.3 | 0.43333 | 0.3875 | 0.51429 | 0.32222 | 0.3875 | 0.58333 | 0.35 | 0.5 | 0.65 | 0.55714 | 0.68571 | 0.85 | 0.77143 | 1.46 | 1.95 |  | Healthcare | 6 | 6 | 6 | 6 | 6 | 8 | 7 | 9 | 8 | 6 | 8 | 6 | 6 | 7 | 7 | 6 | 7 | 5 | 4
| R-1 | Hotel/Motel | 0.2 | 0.075 | 0.15 | 0.022222 | 0.21818 | 0.18182 | 0.18 | 0.21667 | 0.21538 | 0.18889 | 0.2 | 0.2625 | 0.24444 | 0.23636 | 0.28889 | 0.3125 | 0.31111 | 0.58571 | 1.04 |  | Hotel/Motel | 9 | 8 | 12 | 9 | 11 | 11 | 10 | 12 | 13 | 9 | 12 | 8 | 9 | 11 | 9 | 8 | 9 | 7 | 5
| B | Office Buildings | 0.16429 | 0.12143 | 0.094118 | 0.12 | 0.076471 | 0.068421 | 0.072222 | 0.1 | 0.095833 | 0.17059 | 0.15455 | 0.1875 | 0.25 | 0.21111 | 0.22778 | 0.28571 | 0.22353 | 0.35 | 0.58182 |  | Office | 14 | 14 | 17 | 15 | 17 | 19 | 18 | 22 | 24 | 17 | 22 | 16 | 14 | 18 | 18 | 14 | 17 | 14 | 11
| A-2 | Restaurant Buildings | 0.35 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35 | 0 | 0 | 0.95 | 0.23333 | 0.15 | 1.5 | 0.85 | 2.35 | 5.9 |  | Restaurant | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 4 | 2 | 3 | 2 | 2 | 3 | 2 | 2 | 2 | 2 | 1
| M | Retail Buildings | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13333 |  | Retail | 8 | 8 | 12 | 9 | 11 | 12 | 12 | 17 | 17 | 11 | 13 | 9 | 10 | 11 | 10 | 9 | 10 | 9 | 6
| E | Education Buildings | 0.22 | 0.2 | 0.22308 | 0.225 | 0.20769 | 0.1625 | 0.11333 | 0.14762 | 0.16818 | 0.19333 | 0.21579 | 0.20667 | 0.22857 | 0.20588 | 0.19375 | 0.22308 | 0.19375 | 0.36667 | 0.52 |  | School/Education | 10 | 11 | 13 | 12 | 13 | 16 | 15 | 21 | 22 | 15 | 19 | 15 | 14 | 17 | 16 | 13 | 16 | 12 | 10
| S-1, S-2 | Warehouse | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.12069 | 0.041463 | 0 | 0.19583 | 0.12187 | 0.21304 | 0.3375 |  | Warehouse | 38 | 37 | 55 | 45 | 53 | 53 | 49 | 58 | 66 | 36 | 56 | 38 | 29 | 41 | 36 | 24 | 32 | 23 | 16
Load Management Points available for carryover net of revised (lowered) requirement (CED1-188)
Surplus LM (G01,G02,G06) after meet LM/PV requirements with only LM
| Building Occupancy Group |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | SA | SB | SC | 6A | 6B | 7 | 8
| R-2, R-4, and 1-1 | Multi-family/Dormitory | 41 | 28 | 18 | 19 | 6 | 16 | 12 | 6 | 24 | 16 | 26 | 27 | 21 | 19 | 23 | 10 | 12 | 15 | 20
| I-2 | Healthcare | 2 | 3 | 2 | 2 | 0 | 9 | 0 | -4 | 1 | 3 | 6 | 4 | 4 | 4 | 3 | 4 | 1 | 3 | 3
| R-1 | Hotel/Motel | 7 | 9 | 4 | 8 | 6 | 7 | 9 | 6 | 5 | 11 | 6 | 15 | 10 | 7 | 13 | 10 | 10 | 11 | 14
| B | Office Buildings | -23 | -13 | -18 | -15 | -19 | -29 | -21 | -25 | -33 | -15 | -29 | -14 | -12 | -19 | -16 | -14 | -18 | -12 | -14
| A-2 | Restaurant Buildings | 41 | 35 | 48 | 38 | 42 | 38 | 39 | 33 | 34 | 32 | 28 | 29 | 31 | 25 | 24 | 27 | 26 | 24 | 12
| M | Retail Buildings | -13 | -13 | -4 | 0 | -3 | -14 | -5 | -9 | -16 | 5 | -7 | 10 | 1 | 1 | 11 | 0 | 1 | 4 | -6
| E | Education Buildings | 3 | 5 | 12 | 4 | 5 | 5 | 3 | -9 | -16 | 0 | 0 | 2 | -1 | 4 | -12 | -1 | 2 | -1 | -5
| S-1 and S-2 | Warehouse | -55 | -15 | -18 | -22 | -26 | -16 | -21 | -27 | -28 | -33 | -42 | -37 | -39 | -51 | -53 | -32 | -54 | -34 | -27
| All Other |  | 9 | 7 | 2 | 4 | -1 | -2 | -2 | -7 | -11 | 3 | -4 | 4 | 3 | -1 | -2 | 1 | -1 | 3 | -1
Restaurant Building example
|  | Carryover Needed | 9 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 9 | 5 | 5 | 21 | 9 | 5 | 32 | 19 | 49 | 61
|  | Surplus LM Points (No PV) | 41 | 35 | 48 | 38 | 42 | 38 | 39 | 33 | 34 | 32 | 28 | 29 | 31 | 25 | 24 | 27 | 26 | 24 | 12
| 0.15 | LM Credits applyable | 6.15 | 5 | 5 | 5 | 5 | 5 | 5 | 4.95 | 5 | 4.8 | 4.2 | 4.35 | 4.65 | 3.75 | 3.6 | 4.05 | 3.9 | 3.6 | 1.8
| 0.3 |  | 9 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 9 | 5 | 5 | 9.3 | 7.5 | 5 | 8.1 | 7.8 | 7.2 | 3.6
| 0.5 |  | 9 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 9 | 5 | 5 | 15.5 | 9 | 5 | 13.5 | 13 | 12 | 6
| 0.7 | Agreed to adjustment | 9 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 9 | 5 | 5 | 21 | 9 | 5 | 18.9 | 18.2 | 16.8 | 8.4
| 1 |  | 9 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 9 | 5 | 5 | 21 | 9 | 5 | 27 | 19 | 24 | 12
|  |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
|  | Renewable Credits per 0.1 W/sf | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 4 | 2 | 3 | 2 | 2 | 3 | 2 | 2 | 2 | 2 | 1
| 0.15 | Renewable needed W/sf | 0.1425 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0016667 | 0 | 0.21 | 0.026667 | 0.0325 | 0.8175 | 0.175 | 0.07 | 1.3975 | 0.755 | 2.27 | 5.92 | 1.5
| 0.3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.585 | 0.05 | 0 | 1.195 | 0.56 | 2.09 | 5.74
| 0.5 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.275 | 0 | 0 | 0.925 | 0.3 | 1.85 | 5.5
| 0.7 | Agreed to adjustment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.655 | 0.04 | 1.61 | 5.26
| 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.25 | 0 | 1.25 | 4.9
Health building example
|  | Carryover Needed | 30 | 25 | 26 | 20 | 28 | 33 | 38 | 31 | 33 | 37 | 30 | 32 | 41 | 41 | 50 | 53 | 56 | 75 | 80
|  | Surplus LM Points (No PV) | 2 | 3 | 2 | 2 | 0 | 9 | 0 | -4 | 1 | 3 | 6 | 4 | 4 | 4 | 3 | 4 | 1 | 3 | 3
| 0.15 | LM Credits applyable | 0.3 | 0.45 | 0.3 | 0.3 | 0 | 1.35 | 0 | 0 | 0.15 | 0.45 | 0.9 | 0.6 | 0.6 | 0.6 | 0.45 | 0.6 | 0.15 | 0.45 | 0.45
| 0.3 |  | 0.6 | 0.9 | 0.6 | 0.6 | 0 | 2.7 | 0 | 0 | 0.3 | 0.9 | 1.8 | 1.2 | 1.2 | 1.2 | 0.9 | 1.2 | 0.3 | 0.9 | 0.9
| 0.5 |  | 1 | 1.5 | 1 | 1 | 0 | 4.5 | 0 | 0 | 0.5 | 1.5 | 3 | 2 | 2 | 2 | 1.5 | 2 | 0.5 | 1.5 | 1.5
| 0.7 | Agreed to adjustment | 1.4 | 2.1 | 1.4 | 1.4 | 0 | 6.3 | 0 | 0 | 0.7 | 2.1 | 4.2 | 2.8 | 2.8 | 2.8 | 2.1 | 2.8 | 0.7 | 2.1 | 2.1
| 1 |  | 2 | 3 | 2 | 2 | 0 | 9 | 0 | 0 | 1 | 3 | 6 | 4 | 4 | 4 | 3 | 4 | 1 | 3 | 3
|  |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
|  | Renewable Credits per 0.1 W/sf | 6 | 6 | 6 | 6 | 6 | 8 | 7 | 9 | 8 | 6 | 8 | 6 | 6 | 7 | 7 | 6 | 7 | 5 | 4
| 0.15 | Renewable needed W/sf | 0.495 | 0.40917 | 0.42833 | 0.32833 | 0.46667 | 0.39563 | 0.54286 | 0.34444 | 0.41063 | 0.60917 | 0.36375 | 0.52333 | 0.67333 | 0.57714 | 0.70786 | 0.87333 | 0.79786 | 1.491 | 1.9888 | 1.5
| 0.3 |  | 0.49 | 0.40167 | 0.42333 | 0.32333 | 0.46667 | 0.37875 | 0.54286 | 0.34444 | 0.40875 | 0.60167 | 0.3525 | 0.51333 | 0.66333 | 0.56857 | 0.70143 | 0.86333 | 0.79571 | 1.482 | 1.9775
| 0.5 |  | 0.48333 | 0.39167 | 0.41667 | 0.31667 | 0.46667 | 0.35625 | 0.54286 | 0.34444 | 0.40625 | 0.59167 | 0.3375 | 0.5 | 0.65 | 0.55714 | 0.69286 | 0.85 | 0.79286 | 1.47 | 1.9625
| 0.7 | Agreed to adjustment | 0.47667 | 0.38167 | 0.41 | 0.31 | 0.46667 | 0.33375 | 0.54286 | 0.34444 | 0.40375 | 0.58167 | 0.3225 | 0.48667 | 0.63667 | 0.54571 | 0.68429 | 0.83667 | 0.79 | 1.458 | 1.9475
| 1 |  | 0.46667 | 0.36667 | 0.4 | 0.3 | 0.46667 | 0.3 | 0.54286 | 0.34444 | 0.4 | 0.56667 | 0.3 | 0.46667 | 0.61667 | 0.52857 | 0.67143 | 0.81667 | 0.78571 | 1.44 | 1.925
Education Building example
|  | Carryover Needed | 24 | 24 | 31 | 29 | 29 | 28 | 19 | 33 | 39 | 31 | 43 | 33 | 34 | 37 | 33 | 31 | 33 | 46 | 54
|  | Surplus LM Points (No PV) | 3 | 5 | 12 | 4 | 5 | 5 | 3 | -9 | -16 | 0 | 0 | 2 | -1 | 4 | -12 | -1 | 2 | -1 | -5
| 0.15 | LM Credits applyable | 0.45 | 0.75 | 1.8 | 0.6 | 0.75 | 0.75 | 0.45 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0.6 | 0 | 0 | 0.3 | 0 | 0
| 0.3 |  | 0.9 | 1.5 | 3.6 | 1.2 | 1.5 | 1.5 | 0.9 | 0 | 0 | 0 | 0 | 0.6 | 0 | 1.2 | 0 | 0 | 0.6 | 0 | 0
| 0.5 |  | 1.5 | 2.5 | 6 | 2 | 2.5 | 2.5 | 1.5 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 0 | 0 | 1 | 0 | 0
| 0.7 | Agreed to adjustment | 2.1 | 3.5 | 8.4 | 2.8 | 3.5 | 3.5 | 2.1 | 0 | 0 | 0 | 0 | 1.4 | 0 | 2.8 | 0 | 0 | 1.4 | 0 | 0
| 1 |  | 3 | 5 | 12 | 4 | 5 | 5 | 3 | 0 | 0 | 0 | 0 | 2 | 0 | 4 | 0 | 0 | 2 | 0 | 0
|  |  | 0A | 0B | 1A | 1B | 2A | 2B | 3A | 3B | 3C | 4A | 4B | 4C | 5A | 5B | 5C | 6A | 6B | 7 | 8
|  | Renewable Credits per 0.1 W/sf | 10 | 11 | 13 | 12 | 13 | 16 | 15 | 21 | 22 | 15 | 19 | 15 | 14 | 17 | 16 | 13 | 16 | 12 | 10
| 0.15 | Renewable needed W/sf | 0.2355 | 0.21136 | 0.22462 | 0.23667 | 0.21731 | 0.17031 | 0.12367 | 0.15714 | 0.17727 | 0.20667 | 0.22632 | 0.218 | 0.24286 | 0.21412 | 0.20625 | 0.23846 | 0.20438 | 0.38333 | 0.54 | 1.5
| 0.3 |  | 0.231 | 0.20455 | 0.21077 | 0.23167 | 0.21154 | 0.16562 | 0.12067 | 0.15714 | 0.17727 | 0.20667 | 0.22632 | 0.216 | 0.24286 | 0.21059 | 0.20625 | 0.23846 | 0.2025 | 0.38333 | 0.54
| 0.5 |  | 0.225 | 0.19545 | 0.19231 | 0.225 | 0.20385 | 0.15937 | 0.11667 | 0.15714 | 0.17727 | 0.20667 | 0.22632 | 0.21333 | 0.24286 | 0.20588 | 0.20625 | 0.23846 | 0.2 | 0.38333 | 0.54
| 0.7 | Agreed to adjustment | 0.219 | 0.18636 | 0.17385 | 0.21833 | 0.19615 | 0.15313 | 0.11267 | 0.15714 | 0.17727 | 0.20667 | 0.22632 | 0.21067 | 0.24286 | 0.20118 | 0.20625 | 0.23846 | 0.1975 | 0.38333 | 0.54
| 1 |  | 0.21 | 0.17273 | 0.14615 | 0.20833 | 0.18462 | 0.14375 | 0.10667 | 0.15714 | 0.17727 | 0.20667 | 0.22632 | 0.20667 | 0.24286 | 0.19412 | 0.20625 | 0.23846 | 0.19375 | 0.38333 | 0.54

## Sheet1 (hidden)
CBECS 2016 |  |  |  | Trillion BTU |  |  |  |  | CBECS 2016, Table C1
| Bldg | Floor Area | Sum Fuels | EL Source | El Site | Gas | Oil | DH | Built Thru | Site EL | Gas + Oil | % Fossil
Before 1920 | 329 | 3600 | 238 | 349 | 120 | 81 | 15 | 22 | 1920 | 120 | 96 | 0.44444
1920 to 1945 | 379 | 5646 | 401 | 643 | 222 | 124 | 14 | 41 | 1945 | 222 | 138 | 0.38333
1946 to 1959 | 517 | 6937 | 446 | 657 | 227 | 173 | 12 | 35 | 1959 | 227 | 185 | 0.44903
1960 to 1969 | 685 | 10360 | 764 | 1185 | 409 | 289 | 11 | 56 | 1969 | 409 | 300 | 0.42313
1970 to 1979 | 831 | 13061 | 905 | 1579 | 545 | 303 | 13 | 45 | 1979 | 545 | 316 | 0.36702
1980 to 1989 | 794 | 13465 | 965 | 1793 | 618 | 312 | 7 | 27 | 1989 | 618 | 319 | 0.34045
1990 to 1999 | 921 | 15535 | 959 | 1767 | 609 | 312 | 13 | 25 | 1999 | 609 | 325 | 0.34797
2000 to 2009 | 924 | 17500 | 1399 | 2509 | 865 | 476 | 12 | 46 | 2009 | 865 | 488 | 0.36068
2010 to 2018 | 537 | 10319 | 730 | 1378 | 475 | 232 | 4 | 19 | 2018 | 475 | 236 | 0.33193