# CARBON MONOXIDE ALARM FIELD STUDY

December 22, 2004

Report by: Sean Moloney

Reviewed by: Paul Patty

Copyright © 2005 Underwriters Laboratories Inc.

INTRODUCTION:

In March 1999, UL initiated a Carbon Monoxide (CO) Alarm Field Study to monitor the effective performance of currently available CO alarms.  This study was developed to evaluate the possible drift of sensors and CO alarm effectiveness.  The study involved the collection of numerous UL Listed CO alarms from manufacturer locations and U.S retail stores by the UL Field Services staff.  All CO alarms were UL Listed in accordance with the Standard for Single and Multiple Station Carbon Monoxide Alarms, UL2034.  This study was completed after the March 2004 testing,.

Initial sensitivity tests were recorded and the alarms were then distributed to UL staff and the alarm’s installed locations were noted.  At the specified frequencies UL staff returned their assigned CO alarms for sensitivity testing.

SAMPLES:

Samples were selected to represent the following three current types of sensor technologies: (1) electrochemical, (2) biomemetic, and (3) semiconductor.  Samples were also chosen based on their manufactured date of either prior or post Oct. 1, 1998.

A total of 70 CO alarms were distributed to UL staff.  Of the 70 samples, 43 samples were manufactured prior to Oct. 1, 1998.  Not all of the 70 samples were returned at the specified frequency for testing.  For the most recent sample pick up, data was recorded for 45 CO alarms.

See attached 2004 Addendum 1 for detailed information for each CO alarm such as sample number, sensor technology, etc.

TESTS CONDUCTED:

Samples that were manufactured prior to Oct. 1, 1998 were subjected to the Sensitivity Test according to paragraph 38 of UL2034 (Oct. 15, 1997).  The samples were exposed to a concentration of Carbon Monoxide of 100ppm, 200ppm, and 400ppm.  UL2034 specifies that the units must alarm between 16-90 minutes, 8-35 minutes, and 4-15 minutes respectively for each CO concentration.  A false alarm Stability Test was also conducted at 15ppm for 8 hours.

Samples that were manufactured post Oct. 1, 1998 were subjected to the Sensitivity Test and Low Humidity Test according to paragraph 38 and 46A.2 of UL2034 (Oct. 1, 1998).  For the Sensitivity Test the samples were exposed to a concentration of Carbon Monoxide of 70ppm, 150ppm, and 400ppm.  UL2034 specifies that units must alarm between 60-240 minutes, 10-50 minutes, and 4-15 minutes respectively for each CO concentration.  A false alarm Stability Test was also conducted at 30ppm for 8 hours.  For the Low Humidity Test units were placed in the low humidity condition of 15  5 %RH for 7 days and after conditioning, while still in the low humidity condition, subjected to the Sensitivity Test as described above.

## The schedule of testing after the initial March 1999 Sensitivity and Low Humidity Tests included the following dates: July 1999, Oct. 1999, March 2000, Sept. 2000, March 2001, Sept. 2001, March 2002, Sept. 2002, March 2003, Sept. 2003, and March 2004.

# CARBON MONOXIDE ALARM FIELD STUDY

DATA:

See attached 2004 Addendum 2 for all response time data developed.  See attached 2004 Addendum 3 for low humidity response time data on samples manufactured post Oct. 1, 1998.

SUMMARY:

Throughout the first phase of this study, the CO alarms have performed in an effective manor.  During the September 2002 tests we recorded our first false positive at 70ppm CO (94 minutes into the test, post 1998 alarm).  Also during the September 2002 tests we recorded our first no response sample (pre1998 alarm).  During the September 2003 we recorded a significant late response sample (pre1998 alarm).  These samples have been returned and analyzed by the manufacturer and/or the UL Field Report Group has opened an investigation.  Other samples in the survey of the same, or similar, models are continuing to perform as expected.

On one occasion, a field study CO sample alarmed in an employee’s home after their furnace was serviced.  It was confirmed that there was a high level of CO present in their home.  The problem was corrected and the alarm continues to function properly during follow-up sensitivity tests.  On another occasion, a field sample was activated when the damper on a fireplace closed prematurely.  The damper was opened, the house vented, and the alarm returned to its normal standby condition.

Throughout the entire survey program we have experienced a few units providing early/delayed signals during the sensitivity tests, but all of these CO alarms would provide effective signaling protection to the users should there be a fatal concentration of CO.

Of the few CO alarms that did not meet the UL2034 test points, most of them alarmed early and it was determined with the Stability Test results that these samples would most likely not false alarm in the field.

It is important to note that providing effective signaling protection does not necessarily mean complying with the finite test points of UL2034.  All the alarms would have sounded while a person can react and follow the recommended procedures during an alarm signal.

The data shows that these CO alarms are providing the necessary signaling protection.

### 2004 Addendum 1

| # Sample | UL 2034 | Sensor | Power Source |
| --- | --- | --- | --- |
| 001R | Oct-95 | Tin Oxide | 120 Vac |
| 002R | Oct-95 | Tin Oxide | 120 Vac |
| 003R | Oct-95 | Tin Oxide | 120 Vac |
| 004R | Oct-98 | Tin Oxide | 120 Vac |
| 005R | Oct-98 | Tin Oxide | 120 Vac |
| 006R | Oct-95 | Biomimetic | 9 V Battery |
| 007R | Oct-95 | Biomimetic | 9 V Battery |
| 008R | Oct-98 | Electrochemical | 120 Vac |
| 009R | Oct-98 | Electrochemical | 120 Vac |
| 010R | Oct-95 | Tin Oxide | 120 Vac |
| 011R | Oct-95 | Tin Oxide | 120 Vac |
| 012R | Oct-98 | Electrochemical | 120 Vac w/ 9 V Battery |
| 013R | Oct-98 | Electrochemical | 120 Vac w/ 9 V Battery |
| 014R | Oct-98 | Electrochemical | 120 Vac w/ 9 V Battery |
| 015R | Oct-98 | Electrochemical | 120 Vac w/ 9 V Battery |
| 016R | Oct-95 | Electrochemical | (3) 1.5 V Batteries |
| 017R | Oct-95 | Electrochemical | (3) 1.5 V Batteries |
| 018R | Oct-95 | Tin Oxide | 120 Vac |
| 019R | Oct-95 | Tin Oxide | 120 Vac |
| 020R | Oct-95 | Tin Oxide | 120 Vac |
| 021R | Oct-95 | Tin Oxide | 120 Vac |
| 022-TL | Oct-95 | Biomimetic | 9V BATTERY |
| 023-TL | Oct-95 | Biomimetic | 9V BATTERY |
| 024-TL | Oct-95 | Biomimetic | 9V BATTERY |
| 025-TL | Oct-95 | Biomimetic | 9V BATTERY |
| 026-R | Oct-95 | Biomimetic | 9V BATTERY |
| 027-R | Oct-95 | Biomimetic | 9V BATTERY |
| 028-R | Oct-95 | Biomimetic | 9V BATTERY |
| 029-M | Oct-98 | Electrochemical | 9V BATTERY |
| 030-M | Oct-98 | Electrochemical | 9V BATTERY |
| 031-M | Oct-98 | Electrochemical | 9V BATTERY |
| 032-M | Oct-98 | Tin Oxide | 120Vac |
| 033-M | Oct-98 | Tin Oxide | 120Vac |
| 034-M | Oct-98 | Tin Oxide | 120Vac |
| 035-M | Oct-98 | Tin Oxide | 120Vac |
| 036-M | Oct-98 | Tin Oxide | 120Vac |
| 037-M | Oct-98 | Tin Oxide | 120Vac |
| 038-M | Oct-98 | Tin Oxide | 12VDC |
| 039-M | Oct-98 | Tin Oxide | 12VDC |
| 040-M | Oct-98 | Tin Oxide | 12VDC |
| 041-M | Oct-95 | Biomimetic | 9V BATTERY |
| 042-M | Oct-95 | Biomimetic | 9V BATTERY |
| 043-M | Oct-95 | Biomimetic | 9V BATTERY |
| 044-R | Oct-95 | Electrochemical | 9V BATTERY |
| 045-R | Oct-98 | Electrochemical | 9V BATTERY |
| 046-R | Oct-95 | Biomimetic | 9V BATTERY |
| 047-R | Oct-95 | Biomimetic | 9V BATTERY |
| 048-R | Oct-95 | Biomimetic | 9V BATTERY |
| 049-R | Oct-95 | Biomimetic | 9V BATTERY |
| 050-R | Oct-95 | Biomimetic | 9V BATTERY |
| Sample | UL 2034 | Sensor | Power Source |
| 051-R | Oct-95 | Biomimetic | 9V BATTERY |
| 052-R | Oct-95 | Biomimetic | 9V BATTERY |
| 053-R | Oct-95 | Biomimetic | 9V BATTERY |
| 054-R | Oct-95 | Biomimetic | 9V BATTERY |
| 055-R | Oct-95 | Biomimetic | 9V BATTERY |
| 056-R | Oct-95 | Biomimetic | 9V BATTERY |
| 057-R | Oct-95 | Biomimetic | 9V BATTERY |
| 058-M | Oct-98 | Tin Oxide | 120VAC Hard Wire |
| 059-M | Oct-98 | Tin Oxide | 120VAC Hard Wire |
| 060-M | Oct-98 | Tin Oxide | 120 VAC Hard Wire |
| 061-M | Oct-98 | Tin Oxide | 120VAC Hard Wire |
| 062-M | Oct-98 | Tin Oxide | 120VAC Hard Wire |
| 063-M | Oct-98 | Tin Oxide | 120VAC Hard Wire |
| 064-M | Oct-98 | Tin Oxide | 120VAC |
| 065-M | Oct-98 | Tin Oxide | 120VAC |
| 066-M | Oct-98 | Tin Oxide | 120VAC |
| 067-M | Oct-95 | Tin Oxide | 120VAC |
| 068-M | Oct-95 | Tin Oxide | 120VAC |
| 069/M | Oct-95 | Tin Oxide | 120VAC |
| 070/M | Oct-98 | Nighthhawk | 3-1.5 VAC |
| 071/M | Oct-98 | Electrochemical | 3-1.5 VAC |
| 072/M | Oct-98 | Electrochemical | 3-1.5 VAC |
| 073 | Oct-98 | Electrochemical | 120VAC |
| 074 | Oct-98 | Electrochemical | 120VAC |
| 075 | Oct-98 | Electrochemical | 120VAC |
| 076 | Oct-98 | Electrochemical | 3-"AA" |
| 077 | Oct-98 | Electrochemical | 3-"AA" |
| 078 | Oct-98 | Electrochemical | 3-"AA" |
| 079 | Oct-98 | Electrochemical | 120VAC |
| 080 | Oct-98 | Electrochemical | 120VAC |
| 081 | Oct-98 | Electrochemical | 120VAC |
| 082 | Oct-98 | Electrochemical | 120VAC |
| 083 | Oct-98 | Electrochemical | 120VAC |
| 084 | Oct-98 | Electrochemical | 120VAC |
| 085 | Oct-98 | Electrochemical | 120VAC |
| 086 | Oct-98 | Electrochemical | 120VAC |
| 087 | Oct-98 | Electrochemical | 120VAC |
| 088 | Oct-98 | Electrochemical | 120VAC |
| 089 | Oct-98 | Electrochemical | 120VAC |
| 090 | Oct-98 | Electrochemical | 120VAC |
| 091/R | Oct-95 | Tin Oxide | 120VAC |
| 092/R | Oct-95 | Tin Oxide | 120VAC |
| 093/R | Oct-95 | Tin Oxide | 120VAC |
| 094/R | Oct-95 | Biomimetic | 9V BATTERY |
| 095/R | Oct-95 | Biomimetic | 9VDC (Sensor Pak) |
| 096/R | Oct-95 | Tin Oxide | 120VAC |
| 097/R | Oct-95 | Biomimetic | 9V BATTERY |
| 098/R | Oct-95 | Biomimetic | 9V BATTERY |
| 099/R | Oct-95 | Biomimetic | 9V BATTERY |
| 100/R | Oct-95 | Biomimetic | 9VDC (Sensor Pak) |
| Sample | UL 2034 | Sensor | Power Source |
| 101/R | Oct-95 | Biomimetic | 9VDC (Sensor Pak) |
| 102/R | Oct-95 | Biomimetic | 9VDC (Sensor Pak) |
| 103 | Oct-95 | Biomimetic | 9V BATTERY |
| 104-R | Oct-95 | Biomimetic | 9V BATTERY |
| 105 | Oct-95 | Biomimetic | 9V BATTERY |
| 106-R | Oct-95 | Tin Oxide | 120 VAC |
| 107-R | Oct-95 | Biomimetic | 9V BATTERY |
| 108-R | Oct-95 | Biomimetic | 9V BATTERY |
| 109-R | Oct-95 | Biomimetic | 9V BATTERY |
| 110-R | Oct-95 | Biomimetic | 9V BATTERY |
| 111-R | Oct-95 | Biomimetic | 9V BATTERY |
| 112-R | Oct-95 | Biomimetic | 9V BATTERY |
| 113-R | Oct-95 | Electrochemical | 2 1.5V "AA" |
| 114 | Oct-95 | Electrochemical | 2 1.5V "AA" |
| 115 | Oct-95 | Electrochemical | 2 1.5V "AA" |
| 116-R | Oct-95 | Biomimetic | 9V BATTERY |
| 117-R | Oct-95 | Biomimetic | 9V BATTERY |
| 118-R | Oct-95 | Biomimetic | 9V BATTERY |
| 119-R | Oct-95 | Tin Oxide | 120 VAC |
| 120-R | Oct-95 | Tin Oxide | 120 VAC |
| 121-R | Oct-95 | Tin Oxide | 120 VAC |
| 122-R | Oct-95 | Biomimetic | 9VDC Battery |
| 123-R | Oct-95 | Biomimetic | 9VDC Battery |
| 124-R | Oct-95 | Biomimetic | 9VDC Battery |
| 125-R | Oct-95 | Biomimetic | 9V BATTERY |
| 126-R | Oct-95 | Biomimetic | 9V BATTERY |
| 127-R | Oct-95 | Biomimetic | 9V BATTERY |
| 128 | Oct-95 | Tin Oxide | 120VAC |
| 129 | Oct-95 | Tin Oxide | 120VAC |
| 130-M | Oct-98 | Tin Oxide | 120VAC |
| 131-M | Oct-98 | Tin Oxide | 120VAC |
| 132-M | Oct-98 | Tin Oxide | 120VAC |
| 133 | Oct-98 | Biomimetic | 12VDC |
| 134 | Oct-95 | Biomimetic | 12VDC |
| 135 | Oct-95 | Biomimetic | 12VDC |
| 136 | N/A | N/A | N/A |
| 137 | Oct-95 | Biomimetic | 9V Battery Pack |
| 138 | Oct-95 | Biomimetic | 9V Battery Pack |
| 139 | Oct-95 | Biomimetic | 9V Battery Pack |
| 140 | Oct-95 | Biomimetic | 9V Battery Pack |
| 141 | Oct-95 | Biomimetic | 9V Battery Pack |

#### 2004 Addendum 2

Sample Number: 001

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		45:36		28:48		13:13

July 1999		60:12		30:49		14:48

Oct. 1999		No alarm	83:00		28:21

March 2000		69:00		28:52		14:48

Sept. 2000		70:00		27:36		13:49

March 2001		69:00		30:02		14:56

Sept. 2001		68:00		29:37		14:23

March 2002		No alarm	34:53		14:57

Sept. 2002		No alarm	114:00		29:05

March 2003		No Alarm	120:00		28:02

Sept. 2003		No Alarm	No Alarm	1:11

March 2004		No Alarm	No Alarm	88:00

Note: Sample was affected in a home fire around the March 2002 testing.

Sample Number: 002

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		30:29		13:28		8:25

July 1999		49:51		25:35		13:10

Oct. 1999		No alarm	70:00		29:30

March 2000		59:26		28:51		14:19

Sept. 2000		30:09		27:36		13:49

March 2001		29:00		25:04		12:43

Sept. 2001		29:47		28:31		8:04

March 2002		29:23		14:12		7:16

Sept. 2002		29:16		24:49		8:31

March 2003		29:22		28:33		11:31

Sept. 2003		33:13		20:18		13:59

March 2004		30:22		13:27		10:46

Sample Number: 003

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		30:20		12:54		10:37

July 1999		60:09		25:42		13:55

Oct. 1999		149:00		69:00		27:43

March 2000		69:00		29:20		14:09

Sept. 2000		69:00		27:34		13:49

March 2001		59:00		30:03		14:39

Sept. 2001		31:06		30:18		13:08

March 2002		68:00		28:37		14:20

Sept. 2002		65:00		28:20		9:15

March 2003		32:36		29:40		13:45

Sept. 2003		28:39		30:27		14:21

March 2004		33:12		30:30		25:11

Sample Number: 004

# Response Time in Minutes

Sensitivity		70 ppm CO 	150 ppm CO	400 ppm CO

## March 1999		81:31		22:12		6:29

July 1999		23:22		15:25		6:10

Oct. 1999		58:13		21:55		10:32

March 2000		26:44		10:28		5:32

Sept. 2000		65:00		10:25		9:14

March 2001		64:00		11:39		8:42

Sept. 2001		35:21		10:53		4:39

March 2002		68:00		18:55		14:10

Sept. 2002		140:00		24:26		14:48

March 2003		121:00		22:32		12:21

Sept. 2003		No Alarm	No Alarm	117:00

March 2004		Note: Sent back to mfg for analysis; and

Supervised failure in field - trouble signal.

Sample Number: 005

# Response Time in Minutes

Sensitivity		70 ppm CO 	150 ppm CO	400 ppm CO

## March 1999		81:34		21:51		5:53

July 1999		22:48		20:56		6:05

Oct. 1999		41:37		24:38		24:56

March 2000		25:12		20:04		5:24

Sept. 2000		24:41		18:27		4:22

March 2001		21:05		17:58		5:29

Sept. 2001		18:38		12:38		4:41

March 2002		37:21		23:41		6:09

Sept. 2002		26:14		6:43		5:28

March 2003		Note: No response. Field Report Group has opened an investigation.

Sample Number: 006

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		167:50		20:21		10:28

July 1999		51:38		17:51		6:50

Oct. 1999		45:21		40:45		14:45

March 2000		54:02		21:31		12:06

Sept. 2000		46:53		13:52		7:31

March 2001		50:51		26:46		10:48

Sept. 2001		40:51		22:43		9:59

March 2002		49:23		18:49		13:47

Sept. 2002		48:02		17:58		7:59

March 2003		50:41		19:13		18:22

Sept. 2003		47:57		20:45		10:05

March 2004		53:01		23:22		14:47

Sample Number: 007

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		67:30		2:52		0:36

July 1999		42:45		13:08		4:51

Oct. 1999		44:24		42:16		13:21

March 2000		42:58		19:25		7:14

Sept. 2000		44:34		9:38		5:47

March 2001		40:32		8:55		5:20

Sept. 2001		34:02		9:22		5:29

March 2002		45:10		14:24		11:38

Sept. 2002		43:20		19:15		5:26

March 2003		49:34		14:46		6:32

Sept. 2003		39:58		11:05		5:18

March 2004		44:25		16:30		9:15

Sample Number: 009

# Response Time in Minutes

Sensitivity		70 ppm CO 	150 ppm CO	400 ppm CO

## March 1999		(45) 197:00	(106) 48:41	(314) 13:11

July 1999		(34) No alarm	(80) 60:48	(239) 22:07

Oct. 1999		(0) No alarm	(61) 120:08	(209) 25:35

March 2000		(0) No alarm	(56) 133:00	(172) 30:46

Sept. 2000		(0) No alarm	(50) 153:00	(161) 40:35

March 2001		(0) No alarm	(50) 158:00	(168) 35:39

Sept. 2001		(0) No alarm	(0) No alarm	(103) 57:30

March 2002		(0) No alarm	(0) No alarm	(110) 52:47

Sept. 2002		(0) No alarm	(0) No alarm	(92) 75:00

March 2003		Note: Sample has been recalled in industry.

Sample Number: 010

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		(83) 48:46	(223) 16:32	(358) 8:11

July 1999		(81) 24:24	(156) 22:10	(301) 10:22

Oct. 1999		(50) No alarm	(111) 35:24	(230) 14:22

March 2000		(60) 106:00	(123) 29:50	(154) 22:07

Sept. 2000		(83) 55:15	(163) 19:55	(271) 10:25

March 2001		(87) 55:16	(149) 24:09	(242) 13:34

Sept. 2001		(95) 49:30	(168) 20:46	(302) 10:14

March 2002		Note: Sample out of survey.

Sample Number: 011

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		(83) 52:19	(181) 18:18	(258) 10:57

July 1999		(88) 50:24	(144) 26:22	(229) 14:57

Oct. 1999		(68) 108:00	(81) 52:43	(146) 29:31

March 2000		(70) 78:00	(117) 30:56	(197) 17:24

Sept. 2000		(84) 53:28	(160) 20:03	(282) 11:13

March 2001		(69) 83:00	(122) 30:27	(251) 13:46

Sept. 2001		(66) 85:00	(154) 20:40	(256) 12:13

March 2002		(67) 77:00	(132) 28:16	(228) 12:05

Sept. 2002		(76) 60:00	(135) 24:25	(266) 10:26

March 2003		(69) 79:00	(129) 32:31	(199) 14:57

Sept. 2003		(63) 96:00	(126) 22:28	(220) 14:28

March 2004		(75) 58:16	(135) 25:13	(307) 7:36

Sample Number: 016

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		(78) 68:34	(159) 26:59	(374) 9:52

## July 1999		Note: Unit not yet distributed.  Unit is powered in lab.

Oct. 1999		(77) 60:06	(139) 33:11	(366) 10:16

March 2000		(83) 66:00	(143) 30:15	(292) 12:44

Sept. 2000		(79) 77:00	(152) 27:39	(389) 9:58

March 2001		(81) 62:00	(140) 32:11	(418) 8:32

Sept. 2001		(72) 87:00	(129) 35:48	(253) 14:34

March 2002		(73) 80:00	(134) 33:16	(321) 12:19

Sept. 2002		(75) 73:00	(133) 34:59	(320) 10:56

March 2003		(75) 78:00	(132) 34:52	(279) 13:06

Sept. 2003		(68) 88:00	(132) 34:34	(251) 14:48

March 2004		(130) 35:16	(136) 32:27	(274) 11:19

Sample Number: 017

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		(82) 67:31	(160) 27:50	(379) 11:31

July 1999		(81) 60:10	(144) 27:05	(370) 11:16

Oct. 1999		(81) 70:00	(146) 32:10	(349) 10:44

March 2000		(73) 81:00	(135) 38:29	(311) 13:03

Sept. 2000		(81) 71:00	(151) 29:32	(374) 10:32

March 2001		(85) 66:00	(122) 34:10	(259) 13:45

Sept. 2001		(78) 73:00	(138) 35:52	(367) 7:27

March 2002		(67) 94:00	(123) 34:10	(289) 13:49

Sept. 2002		(106) 64:00	(147) 31:40	(302) 12:10

March 2003		(74) 81:00	(109) 45:22	(184) 12:02

Sept. 2003		(75) 79:00	(128) 44:53	(297) 13:45

March 2004 		(111) 43:09	(115) 40:43	(183) 18:46

Sample Number: 018

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		23:23		7:18		5:31

July 1999		30:22		16:54		7:21

Oct. 1999		24:41		22:35		17:53

March 2000		65:00		24:14		4:20

Sept. 2000		24:04		22:45		4:37

March 2001		23:15		21:16		5:26

Sept. 2001		24:02		15:45		4:35

March 2002		No alarm	22:54		5:17

Sept. 2002		25:31		23:38		4:24

March 2003		24:37		22:49		5:09

Sept. 2003		24:24		22:56		6:46

March 2004		27:31		28:03		7:24

Sample Number: 019

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		22:24		6:52		5:38

July 1999		31:10		17:14		7:23

Oct. 1999		No alarm	23:20		5:57

March 2000		56:41		24:16		4:21

Sept. 2000		23:51		21:42		6:14

March 2001		22:58		18:43		5:32

Sept. 2001		21:48		20:51		5:58

March 2002		24:19		24:11		4:51

Sept. 2003		31:24		26:50		5:07

March 2003		Note: Supervised failure in the field - power on LED de-energized.

Sample Number: 020

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		22:24		6:50		5:53

July 1999		24:39		23:16		5:22

Oct. 1999		No alarm	23:11		4:45

March 2000		28:26		23:44		6:16

Sept. 2000		23:34		21:40		6:07

March 2001		22:53		21:52		5:49

Sept. 2001		Note: No data for sample.

March 2002		22:59		21:38		5:49

Sept. 2002		84:00		23:14		5:16

March 2003		21:52		19:43		5:07

Sept. 2003		22:10		21:45		13:43

March 2004		Note: Sample out of survey.

Sample Number: 021

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		24:54		23:02		5:07

July 1999		22:36		22:01		7:12

Oct. 1999		87:00		22:31		6:05

March 2000		26:45		21:49		6:28

Sept. 2000		25:05		20:42		5:31

March 2001		Note: Sample out of survey.

Sample Number: 026

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		14:45		10:50		4:18

July 1999		6:28		3:38		2:19

Oct. 1999		16:45		14:44		6:45

March 2000		8:21		6:04		4:02

Sept. 2000		8:26		6:53		4:11

March 2001		8:03		6:31		4:08

Sept. 2001		7:52		6:01		4:05

March 2002		4:18		2:08		1:40

Sept. 2002		3:24		1:51		1:21

March 2003		3:20		3:02		2:18

Sept. 2003		3:34		2:26		1:55

March 2004		3:27		2:22		1:49

Sample Number: 027

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		14:21		11:15		3:10

July 1999		5:34		3:40		2:22

Oct. 1999		15:16		11:56		5:16

March 2000		12:15		4:17		6:51

Sept. 2000		11:29		7:51		4:31

March 2001		10:25		7:25		4:24

Sept. 2001		8:48		6:42		4:10

March 2002		4:38		2:40		1:49

Sept. 2002		3:15		1:36		1:12

March 2003		3:32		3:10		2:20

Sept. 2003		3:38		2:24		1:52

March 2004		3:24		2:20		1:48

Sample Number: 028

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		15:53		11:45		4:35

July 1999		5:17		2:43		1:57

Oct. 1999		25:47		12:10		2:59

March 2000		13:44		6:20		4:12

Sept. 2000		9:05		6:23		4:08

March 2001		8:53		6:33		4:06

Sept. 2001		8:15		6:07		3:56

March 2002		5:31		3:47		2:04

Sept. 2002		3:42		1:53		1:15

March 2003		5:24		4:23		2:13

Sept. 2003		6:22		5:16		2:37

March 2004		6:51		5:36		4:36

Sample Number: 029

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		82:55		12:43		11:50

July 1999		Note: Unit not yet distributed.  Unit is powered in lab.

Oct. 1999		83:00		12:02		11:06

March 2000		83:00		11:44		10:47

Sept. 2000		80:00		11:42		10:41

March 2001		73:00		11:29		9:11

Sept. 2001		70:00		11:10		9:14

March 2002		80:00		10:34		10:06

Sept.2002		84:00		11:02		10:20

March 2003		86:00		10:44		10:12

Sept. 2003		80:00		10:41		10:17

March 2004		82:00		11:48		10:04

Sample Number: 030

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		85:54		12:59		12:02

July 1999		Note: Unit not yet distributed.  Unit is powered in lab.

Oct. 1999		86:00		12:23		11:32

March 2000		85:00		11:56		11:20

Sept. 2000		Note: Sample out of survey.

Sample Number: 031

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		85:32		12:45		11:23

July 1999		Note: Supervised failure in field - trouble signal.

Sample Number: 032

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		18:56		7:42		5:14

July 1999		24:40		7:25		5:30

Oct. 1999		44:52		13:50		7:08

March 2000		22:10		10:09		6:10

Sept. 2000		Note: Sample has been removed from survey by UL Field Report Group.

Sample Number: 033

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		58:38		15:56		7:15

July 1999		42:40		19:36		8:07

Oct. 1999		86:00		16:32		5:06

March 2000		31:40		10:42		6:43

Sept. 2000		49:22		14:47		4:54

March 2001		48:35		11:43		4:43

Sept. 2001		Note: Sample out of survey.

Sample Number: 034

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		60:41		19:58		5:50

July 1999		60:35		31:12		6:53

Oct. 1999		72:00		29:35		6:53

March 2000		88:00		19:41		4:15

Sept. 2000		94:00		23:16		5:12

March 2001		90:00		25:23		8:33

Sept. 2001		86:00		29:23		9:21

March 2002		90:00		19:26		8:22

Sept. 2002		89:00		13:31		5:58

March 2003		111:00		18:12		4:41

Sept. 2003		68:00		44:45		12:23

March 2004		Note: Sample out of survey.

Sample Number: 035

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		47:51		15:25		7:02

July 1999		47:27		15:13		6:25

Oct. 1999		86:00		35:27		10:40

March 2000		46:31		19:41		5:50

Sept. 2000		44:23		20:23		4:57

March 2001		42:10		18:53		4:21

Sept. 2001		28:17		10:46		4:17

March 2002		44:30		15:21		4:43

Sept. 2002		14:11		7:12		4:50

March 2003		24:02		8:14		6:34

Sept. 2003		24:30		11:10		5:26

March 2004		27:14		10:42		10:20

Sample Number: 036

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		60:57		15:47		6:20

July 1999		60:05		17:03		7:04

Oct. 1999		90:00		15:34		7:29

March 2000		64:00		27:31		6:39

Sept. 2000		63:00		21:23		5:44

March 2001		64:00		19:40		5:17

Sept. 2001		62:00		12:24		6:34

March 2002		42:05		17:14		4:56

Sept. 2002		15:21		6:29		4:46

March 2003		16:21		7:31		4:58

Sept. 2003		20:25		16:30		5:53

March 2004		16:56		13:51		4:18

Sample Number: 037

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		88:42		21:21		6:36

July 1999		60:30		44:57		9:41

Oct. 1999		60:53		47:46		29:14

March 2000		95:00		56:03		13:24

Sept. 2000		90:00		32:01		5:42

March 2001		86:00		33:14		8:35

Sept. 2001		78:00		30:38		5:58

March 2002		68:00		27:41		5:43

Sept. 2002		62:00		13:43		5:23

March 2003		44:16		14:12		4:59

Sept. 2003		40:23		16:41		5:57

March 2004		57:45		15:21		4:29

Sample Number: 038

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		150:29		21:05		5:57

July 1999		180:10		44:29		10:12

Oct. 1999		105:00		45:32		14:33

March 2000		151:00		43:44		10:35

Sept. 2000		121:00		40:57		6:34

March 2001		122:00		44:51		5:50

Sept. 2001		125:00		42:56		4:52

March 2002		121:00		21:53		6:39

Sept. 2002		102:00		19:07		5:43

March 2003		89:00		19:46		5:24

Sept. 2003		98:00		19:48		6:56

March 2004		90:00		13:46		5:16

Sample Number: 039

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		110:17		21:31		5:35

July 1999		60:53		30:35		6:40

Oct. 1999		102:00		43:40		14:30

March 2000		89:00		28:34		5:42

Sept. 2000		112:00		24:16		7:02

March 2001		91:00		20:24		8:22

Sept. 2001		104:00		29:02		6:40

March 2002		92:00		27:24		5:54

Sept. 2002		89:00		19:41		7:22

March 2003		86:00		21:04		6:16

Sept. 2003		63:00		17:35		5:35

March 2004		75:00		14:54		4:56

Sample Number: 040

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		91:49		17:37		5:43

July 1999		60:37		20:43		7:09

Oct. 1999		76:00		28:35		10:49

March 2000		85:00		18:55		5:41

Sept. 2000		91:00		30:15		7:03

March 2001		88:00		28:01		8:26

Sept. 2001		89:00		20:59		6:40

March 2002		90:00		25:24		5:52

Sept. 2002		80:00		17:15		7:39

March 2003		66:00		18:41		6:18

Sept. 2003		63:00		12:39		5:34

March 2004		71:00		13:13		4:55

Sample Number: 044

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		(85) 66:12	(167) 29:04	(376) 10:49

July 1999		Note: Unit not yet distributed.  Unit is powered in lab.

## Oct. 1999		(88) 62:00	(162) 27:17	(332) 12:50

March 2000		(84) 62:00	(157) 29:35	(320) 12:45

Sept. 2000		(89) 60:00	(148) 30:25	(315) 13:41

March 2001		(83) 62:00	(140) 33:26	(295) 13:12

Set. 2001		(76) 76:00	(130) 34:49	(267) 14:27

March 2002		(69) 77:00	(139) 12:03	(344) 11:14

Sept. 2002		(79) 69:00	(139) 33:10	(355) 10:07

March 2003		(78) 74:00	(134) 34:18	(292) 13:13

Sept. 2003		(76) 78:00	(130) 37:41	(299) 13:20

March 2004		(82) 70:00	(147) 30:47	(337) 10:23

Sample Number: 058

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		100:00		24:29		6:07

July 1999		60:39		23:13		5:52

Oct. 1999		100:00		24:50		8:58

March 2000		95:00		19:33		5:28

Sept. 2000		99:00		23:33		9:37

March 2001		101:00		22:32		6:58

Sept. 2001		100:00		24:07		8:17

March 2002		100:00		24:57		8:36

Sept. 2002		99:00		23:27		9:47

March 2003		100:00		16:36		5:48

Sept. 2003		100:00		23:10		8:21

March 2004		67:00		11:10		6:08

Sample Number: 059

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		99:00		23:30		7:59

July 1999		Note: Unit not yet distributed.  Unit is powered in lab.

Oct. 1999		105:00		23:26		8:49

March 2000		92:00		25:19		5:53

Sept. 2000		119:00		30:26		6:39

March 2001		100:00		26:39		6:42

Sept. 2001		115:00		24:10		8:11

March 2002		99:00		24:35		6:04

Sept. 2002		101:00		23:17		8:15

March 2003		100:00		24:16		5:19

Sept. 2003		100:00		23:03		5:54

March 2004		Note: Sample out of survey.

Sample Number: 060

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		99:00		23:42		8:09

July 1999		Note: Unit not yet distributed.  Unit is powered in lab.

Oct. 1999		101:00		23:43		5:52

March 2000		99:00		24:18		7:02

Sept. 2000		100:00		24:28		6:16

March 2001		103:00		24:45		6:58

Sept. 2001		113:00		23:32		7:30

March 2002		100:00		36:03		7:55

Sept. 2002		136:00		23:56		6:06

March 2003		100:00		24:10		6:13

Sept. 2003		99:00		25:07		6:58

March 2004		Note: Supervised failure in the field - power on LED de-energized.

Sample Number: 061

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		100:22		26:24		7:26

July 1999		31:15		12:15		7:12

Oct. 1999		101:00		23:26		6:45

March 2000		91:00		23:48		7:17

Sept. 2000		100:00		22:57		6:48

March 2001		93:00		21:38		7:13

Sept. 2001		85:00		19:27		5:15

March 2002		95:00		10:43		6:53

Sept. 2002		103:00		22:24		5:42

March 2003		105:00		10:41		5:35

Sept. 2003		102:00		25:23		6:27

March 2004		99:00		23:31		5:51

Sample Number: 062

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		65:41		26:26 		7:35

July 1999		23:54		10:31		7:19

Oct. 1999		29:20		10:41		4:55

March 2000		99:00		23:16		4:31

Sept. 2000		75:00		20:35		4:38

March 2001		68:00		15:36		4:19

Sept. 2001		45:00		10:16		4:16

March 2002		73:00		18:47		9:46

Sept. 2002		65:00		17:51		4:36

March 2003		Note: Sample out of survey.

Sample Number: 063

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		101:36		26:20		6:44

July 1999		60:40		10:24		9:09

Oct. 1999		100:00		23:15		6:56

March 2000		91:00		21:19		4:42

Sept. 2000		84:00		17:29		4:45

March 2001		82:00		17:51		6:00

Sept. 2001		Note: Supervised failure in the field - power on LED de-energized.

Sample Number: 064

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		27:49		11:51		7:12

July 1999		60:39		23:03		7:55

Oct. 1999		140:00		45:32		9:06

March 2000		95:00		10:08		5:27

Sept. 2000		105:00		30:28		8:50

March 2001		101:00		28:41		6:51

Sept. 2001		100:00		23:55		10:08

March 2002		108:00		24:59		8:37

Sept. 2002		102:00		22:46		7:40

March 2003		100:00		25:19		8:35

Sept. 2003		107:00		23:19		8:24

March 2004		Note: Sample out of survey.

Sample Number: 065

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		25:37		11:29		5:30

## July 1999		24:13		10:30		7:42

Oct. 1999		100:00		29:29		8:17

March 2000		36:54		10:15		5:52

Sept. 2000		100:00		20:44		6:18

March 2001		86:00		23:26		5:16

Sept. 2001		Note: No data for sample.

March 2002		98:00		24:45		6:39

Sept. 2002		100:00		26:51		7:56

March 2003		72:00		21:24		7:06

Sept. 2003		66:00		16:04		6:35

March 2004		Note: Sample out of survey.

Sample Number: 066

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		26:12		11:24		7:20

July 1999		60:30		10:21		6:50

Oct. 1999		60:40		24:57		7:21

March 2000		37:25		10:07		6:02

Sept. 2000		Note: Sample out of survey.

Sample Number: 067

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		40:18		27:36		11:06

July 1999		No alarm	33:51		19:20

Oct. 1999		113:00		40:22		20:56

March 2000		35:32		20:15		4:07

Sept. 2000		33:30		20:14		4:25

March 2001		20:12		11:30		4:11

Sept. 2001		16:53		9:41		4:21

March 2002		17:46		8:39		4:10

Sept. 2002		11:10		6:21		4:07

March 2003		13:22		7:30		3:42

Sept. 2003		13:48		10:53		8:22

March 2004		3:15		2:37		1:53

Sample Number: 068

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		49:20		28:09		13:58

July 1999		No alarm	40:18		22:29

Oct. 1999		28:27		13:16		4:41

March 2000		25:13		14:05		4:33

Sept. 2000		30:16		23:24		8:26

March 2001		63:00		36:11		13:42

Sept. 2001		Note: Supervised failure in the field – power on LED de-energized.

Sample Number: 069

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		46:15		10:25		4:21

July 1999		Note: Unit not yet distributed.  Unit is powered in lab.

Oct. 1999		No alarm	29:56		20:13

March 2000		9:54		6:16		4:40

Sept. 2000		18:56		9:11		4:11

March 2001		18:27		8:55		4:09

Sept. 2001		16:34		8:15		4:06

March 2002		4:40		3:40		3:15

Sept. 2002		5:03		3:03		2:48

March 2003		4:50		3:39		2:18

Sept. 2003		4:42		3:50		2:53

March 2004		16:04		3:51		1:10

Sample Number: 091

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		(114) 37:15	(196) 17:55	(357) 9:01

July 1999		(132) 30:44	(240) 14:35	(443) 7:27

Oct. 1999		(96) 50:02	(158) 25:09	(217) 16:36

March 2000		(104) 41:37	(164) 17:16	(461) 8:16

Sept. 2000		(126) 28:01	(287) 13:40	(602) 4:20

March 2001		(135) 22:23	(288) 12:13	(547) 5:22

Sept. 2001		(177) 20:49	(306) 13:45	(485) 6:10

March 2002		(125) 23:43	(227) 12:40	(480) 6:16

Sept. 2002		(228) 16:37	(461) 8:10	(605) 6:01

March 2003		(183) 20:40	(294) 10:35	(540) 6:19

Sept. 2003		(136) 28:07	(281) 10:35	(737) 4:08

March 2004		(175) 26:07	(385) 8:08	(640) 4:11

Sample Number: 092

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		(79) 60:15	(141) 23:50	(244) 13:34

July 1999		(127) 29:00	(217) 14:08	(385) 8:44

Oct. 1999		(55) 125:00	(90) 47:21	(138) 14:31

March 2000		(97) 53:42	(163) 22:21	(245) 11:17

Sept. 2000		(114) 37:16	(220) 15:14	(364) 8:47

March 2001		(122) 32:36	(232) 12:40	(397) 6:38

Sept. 2001		(135) 26:38	(164) 20:21	(404) 8:17

March 2002		(116) 35:09	(177) 18:36	(375) 8:46

Sept. 2002		(143) 22:27	(215) 13:51	(336) 6:43

March 2003		(137) 27:15	(185) 17:43	(329) 9:31

Sept. 2003		Note: Sample out of survey.

Sample Number: 093

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		(99) 42:44	(177) 18:51	(312) 10:09

July 1999		(81) 60:05	(150) 22:52	(263) 12:58

Oct. 1999		Note: Person was not able to return unit for testing.

March 2000		(91) 45:51	(201) 16:10	(430) 6:08

Sept. 2000		(149) 22:50	(312) 11:31	(673) 4:18

March 2001		(153) 21:47	(289) 10:32	(418) 6:10

Sept. 2001		(127) 22:27	(226) 13:38	(495) 6:27

March 2002		(115) 33:50	(213) 15:41	(406) 7:28

Sept. 2002		(95) 46:51	(169) 22:07	(268) 10:07

March 2003		(94) 51:14	(183) 19:36	(383) 8:52

Sept. 2003		(97) 47:34	(161) 24:25	(242) 13:50

March 2004		Note: Sample out of survey.

Sample Number: 094

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		59:52		22:43		9:55

July 1999		24:58		11:41		6:52

Oct. 1999		52:10		50:48		16:37

March 2000		50:22		18:16		9:15

Sept. 2000		48:43		22:53		6:22

March 2001		42:21		24:31		9:17

Sept. 2001		47:56		34:28		13:02

March 2002		68:00		43:11		40:12

Sept. 2002		86:00		38:51		37:11

March 2003		No Alarm	75:00		40:39

Sept. 2003		No Alarm	No Alarm	81:00

March 2004		Note: Sample out of survey.

Sample Number: 096

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		46:21		27:36		11:51

## July 1999		13:23		9:39		6:38

Oct. 1999		No alarm	12:15		6:10

March 2000		18:11		15:23		6:24

Sept. 2000		18:04		13:51		5:51

March 2001		41:26		18:48		6:45

Sept. 2001		49:14		25:04		11:45

March 2002		44:15		21:07		8:00

Sept. 2002		95:00		34:09		11:51

March 2003		91:00		29:18		12:34

Sept. 2003		42:45		23:46		7:24

March 2004		45:22		26:28		10:41

Sample Number: 097

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		51:27		20:25		9:25

July 1999		Note: Unit not yet distributed.  Unit is powered in lab.

## Oct. 1999		51:36		50:50		18:14

March 2000		55:10		17:41		7:45

Sept. 2000		36:34		9:49		5:41

March 2001		28:15		15:12		4:16

Sept. 2001		28:45		13:45		4:11

March 2002		39:57		16:08		7:26

Sept. 2002		33:46		11:37		8:35

March 2003		40:22		17:31		13:11

Sept. 2003		Note: Sample out of survey.

Sample Number: 098

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		51:58		19:10		8:09

July 1999		Note: Unit not yet distributed.  Unit is powered in lab.

## Oct. 1999		48:06		22:02		11:32

March 2000		47:10		18:19		12:21

Sept. 2000		46:12		14:33		9:28

March 2001		38:02		21:35		6:35

Sept. 2001		44:05		13:57		10:52

March 2002		50:46		37:04		10:36

Sept. 2002		49:50		34:49		10:02

March 2003		62:00		37:44		14:09

Sept. 2003		45:42		33:26		13:08

March 2004		280:00		41:00		38:25

Sample Number: 099

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		161:39		26:31		10:28

July 1999		Note: Unit not yet distributed.  Unit is powered in lab.

## Oct. 1999		45:51		41:21		13:26

March 2000		43:29		23:26		9:23

Sept. 2000		47:54		16:17		9:27

March 2001		48:21		20:14		13:28

Sept. 2001		38:49		17:57		10:09
March 2002		51:40		20:35		13:56

Sept. 2002		48:56		16:52		5:29

March 2003		49:05		18:02		6:35

Sept. 2003		48:12		25:41		11:06

March 2004		50:30		33:22		12:41

Sample Number: 103

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		87:13		25:25		7:46

July 1999		Note: Unit not yet distributed.  Unit is powered in lab.

## Oct. 1999		54:26		50:45		17:38

March 2000		56:57		20:23		10:54

Sept. 2000		53:22		15:36		6:20

March 2001		43:24		10:04		6:20

Sept. 2001		50:44		20:54		8:29

March 2002		49:09		24:20		10:53

Sept. 2002		41:27		16:33		9:52

March 2003		47:12		45:20		13:48

Sept. 2003		45:20		19:09		9:48

March 2004		51:21		45:23		20:12

Sample Number: 104

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		54:22		21:32		7:35

July 1999		Note: Unit not yet distributed.  Unit is powered in lab.

Oct. 1999		53:22		33:19		13:35

March 2000		42:30		26:57		9:52

Sept. 2000		38:36		18:12		5:37

March 2001		32:45		16:19		6:03

Sept. 2001		33:51		15:57		5:43

March 2002		48:22		25:44		15:51

Sept. 2002		47:22		23:14		9:29

March 2003		74:00		46:24		43:28

Sept. 2003		51:02		18:23		9:17

March 2004		44:43		14:50		10:21

Sample Number: 105

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		73:37		23:41		7:55

July 1999		Note: Unit not yet distributed.  Unit is powered in lab.

Oct. 1999		52:02		20:48		8:20

March 2000		82:00		24:47		11:40

Sept. 2000		52:49		16:15		6:10

March 2001		49:19		14:05		7:29

Sept. 2001		51:33		20:56		8:04

March 2002		126:00		45:49		19:23

Sept. 2002		50:33		42:39		20:45

March 2003		55:32		43:56		20:53

Sept. 2003		68:00		43:16		21:16

March 2004		76:00		51:03		36:44

Sample Number: 106

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		(101) 35:22	(198) 19:25	(375) 7:11

July 1999		(98) 41:20	(179) 19:58	(312) 8:33

Oct. 1999		(97) 50:45	(106) 39:56	(198) 17:15

March 2000		(115) 37:10	(188) 16:25	(325) 9:46

Sept. 2000		(113) 39:12	(241) 11:26	(519) 4:32

March 2001		(127) 33:09	(256) 10:37	(444) 6:09

Sept. 2001		(152) 21:38	(269) 10:08	(426) 5:18

March 2002		(140) 22:45	(243) 13:30	(583) 4:03

Sept. 2002		(121) 32:03	(272) 11:06	(500) 7:01

March 2003		(160) 38:07	(250) 12:40	(626) 5:39

Sept. 2003		(133) 33:02	(212) 19:02	(443) 5:22

March 2004		(108) 38:05	(280) 10:24	(423) 4:55

Sample Number: 116

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		52:07		18:41		7:35

July 1999		55:30		26:43		9:39

Oct. 1999		47:09		29:33		10:20

March 2000		48:24		21:07		12:34

Sept. 2000		43:24		17:10		4:20

March 2001		49:30		27:40		10:12

Sept. 2001		38:16		23:31		10:55

March 2002		37:54		17:58		7:54

Sept. 2002		39:25		14:40		10:29

March 2003		59:26		39:07		24:53

Sept. 2003		41:43		14:40		10:16

March 2004		37:17		30:41		10:52

Sample Number: 117

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		57:32		23:32		8:51

July 1999		51:03		18:19		7:01

Oct. 1999		55:01		22:20		8:58

March 2000		62:00		34:02		8:55

## Sept. 2000		46:57		30:42		6:56

March 2001		56:24		25:40		7:25

Sept. 2001		46:18		13:07		7:38

March 2002		43:35		37:35		15:53

Sept. 2002		46:34		18:51		6:47

March 2003		111:00		33:42		10:58

Sept. 2003		Note: No data for sample.

March 2004		246:00		44:56		36:44

Sample Number: 118

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		50:58		19:20		8:48

July 1999		47:45		18:25		10:45

Oct. 1999		51:37		22:15		12:59

March 2000		48:51		28:14		14:05

## Sept. 2000		48:55		28:02		12:16

March 2001		41:15		22:51		12:37

Sept. 2001		38:26		18:32		7:29

March 2002		50:57		41:26		20:47

Sept. 2002 		52:04		17:22		13:51

March 2003		43:28		39:37		24:53

Sept. 2003		Note: Sample out of survey.

Sample Number: 119

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		24:10		12:21		6:27

July 1999		24:21		6:39		6:30

Oct. 1999		34:26		12:14		4:50

March 2000		29:26		27:07		5:19

Sept. 2000		30:25		24:22		5:29

March 2001		26:37		20:31		5:33

Sept. 2001		20:40		12:37		4:19

March 2002		25:16		18:42		4:40

Sept. 2002		23:45		6:29		4:25

March 2003		23:51		6:39		5:56

Sept. 2003		No alarm	31:32		23:38

March 2004		24:17		5:38		4:13

Sample Number: 120

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		23:42		16:44		5:24

July 1999		No alarm	24:15		24:13

Oct. 1999		No alarm	23:18		6:44

March 2000		24:29		24:08		22:26

Sept. 2000		30:28		21:30		6:37

March 2001		30:40		23:43		6:40

Sept. 2001		28:39		22:43		6:04

March 2002		31:22		23:59		7:35

Sept. 2002		42:23		24:50		14:15

March 2003		23:15		22:51		5:18

Sept. 2003		24:31		22:58		17:55

March 2004		31:05		23:31		21:49

Sample Number: 121

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		22:42		12:07		5:03

July 1999		22:57		20:36		7:30

Oct. 1999		23:13		21:14		16:50

March 2000		23:14		21:57		4:32

Sept. 2000		45:25		32:47		6:51

March 2001		37:40		30:16		5:35

Sept. 2001		21:41		16:54		6:30

March 2002		34:15		28:45		5:22

Sept. 2002	Note: Supervised failure in the field – red normal operation LED indicator flashed irregularly.  Sent back and manufacturer replaced a component.

Sept. 2002(after rework)No alarm	51:02		23:53

March 2003	51:33		36:14		21:45

Sept. 2003	53:37		38:29		21:31

March 2004	Note: Supervised failure in the field – power on LED de-energized.

Sample Number: 125

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		51:40		16:25		8:20

July 1999		60:12		30:49		14:28

Oct. 1999		47:01		20:15		10:04

March 2000		62:00		33:02		12:26

Sept. 2000		45:45		24:45		4:47

March 2001		50:37		27:02		8:35

Sept. 2001		41:22		14:12		7:12

March 2002		40:33		13:19		10:32

Sept. 2002		44:37		15:30		6:13

March 2003		40:54		17:54		13:44

Sept. 2003		37:16		20:58		6:57

March 2004		49:02		27:41		12:10

Sample Number: 126

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		53:02		17:39		8:56

July 1999		Note: Unit not yet distributed.  Unit is powered in lab.

## Oct. 1999		53:21		49:20		16:22

March 2000		86:00		45:48		12:32

Sept. 2000		50:13		27:21		8:55

March 2001		41:11		24:25		8:34

Sept. 2001		42:16		25:21		9:13

March 2002		38:24		19:30		12:41

Sept. 2002		44:18		15:18		6:24

March 2003		45:36		32:45		14:46

Sept. 2003		44:14		26:09		12:36

March 2004		55:25		37:54		8:39

Sample Number: 127

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		53:55		20:36		8:45

July 1999		43:49		22:09		9:20

Oct. 1999		75:00		24:48		10:08

March 2000		67:00		46:04		13:31

Sept. 2000		66:00		46:30		16:16

March 2001		51:22		42:20		14:35

Sept. 2001		82:00		17:11		5:14

March 2002		73:00		43:44		16:32

Sept. 2002		50:07		40:17		21:06

March 2003		82:00		45:22		14:46

Sept. 2003		51:13		39:46		17:35

March 2004		53:16		40:35		15:41

Sample Number: 128

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		22:52		18:23		5:02

July 1999		25:38		22:58		5:58

Oct. 1999		41:55		22:51		7:47

March 2000		49:46		23:22		5:48

Sept. 2000		23:35		21:56		5:40

March 2001		22:33		20:12		4:28

Sept. 2001		24:04		21:14		5:02

March 2002		23:13		22:07		5:41

Sept. 2002		23:10		21:37		5:56

March 2003		24:22		23:11		6:05

Sept. 2003		23:52		22:47		5:10

March 2004		24:16		22:14		5:11

Sample Number: 129

# Response Time in Minutes

Sensitivity		100 ppm CO	200 ppm CO	400 ppm CO

## March 1999		21:57		12:52		4:50

July 1999		22:16		6:49		6:32

Oct. 1999		43:51		27:49		8:45

## March 2000		22:37		8:45		4:51

Sept. 2000		18:16		9:10		4:34

March 2001		17:22		9:27		4:11

Sept. 2001		16:51		8:11		5:17

March 2002		19:09		14:25		5:53

Sept. 2002		6:39		6:10		4:14

March 2003		6:27		6:02		4:35

Sept. 2003		5:29		5:02		4:04

March 2003		6:27		6:02		4:35

Sept. 2003		5:29		5:02		4:04

March 2004		Note: Sample out of survey.

Sample Number: 130

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		77:00		11:30		6:17

July 1999		60:33		12:07		6:46

Oct. 1999		100:00		24:45		6:20

March 2000		97:00		22:02		5:28

Sept. 2000		100:00		20:15		7:15

March 2001		102:00		20:50		6:23

Sept. 2001		104:00		25:31		8:10

March 2002		94:00		21:15		5:16

Sept. 2002		100:00		24:13		5:11

March 2003		102:00		15:24		5:43

Sept. 2003		101:00		12:58		5:45

March 2004		119:00		20:56		5:14

Sample Number: 131

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		76:00		11:32		9:09

July 1999		24:21		9:30		6:25

Oct. 1999		89:00		22:13		8:26

March 2000		101:00		20:46		6:51

Sept. 2000		100:00		18:44		5:13

March 2001		99:00		14:51		6:37

Sept. 2001		101:00		25:50		9:22

March 2002		99:00		18:18		4:34

Sept. 2002		99:00		25:05		8:34

March 2003		94:00		23:26		6:38

Sept. 2003		99:00		23:36		6:06

March 2003		94:00		23:26		6:38

Sept. 2003		101:00		12:58		5:45

March 2004		110:00		25:47		7:43

## Sample Number: 132

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		83:00		11:48		8:25

July 1999		27:09		10:14		7:03

Oct. 1999		98:00		11:16		5:24

March 2000		29:45		10:10		5:15

Sept. 2000		99:00		10:35		5:04

March 2001		96:00		12:22		6:40

Sept. 2001		Note: No data for sample.

March 2002		68:00		24:01		6:18

Sept. 2002		Note: No data for sample.

March 2003		100:00		34:07		8:43

Sept. 2003		Note: Sample out of survey.

(Display Reading)

#### 2004 Addendum 3

Sample Number: 004

# Response Time in Minutes

Sensitivity		70 ppm CO 	150 ppm CO	400 ppm CO

## March 1999		81:29		22:27		6:25

July 1999		25:31		13:39		4:56

Oct. 1999		64:00		22:10		20:48

March 2000		80:00		14:42		9:28

Sept. 2000		62:00		10:30		8:09

March 2001		89:00		14:34		10:25

Sept. 2001		39:52		10:55		7:24

March 2002		94:00		26:24		15:14

Sept. 2002		155:00		30:18		16:24

March 2003		151:00		31:25		14:43

Sept. 2004		Note: No data for sample.

March 2004		Note: Sent back to mfg for analysis; and

Supervised failure in field - trouble signal.

Sample Number: 005

# Response Time in Minutes

Sensitivity		70 ppm CO 	150 ppm CO	400 ppm CO

## March 1999		81:40		21:54		5:56

July 1999		22:45		21:23		5:20

Oct. 1999		90:00		80:00		29:41

March 2000		105:00		23:42		8:51

Sept. 2000		85:00		21:24		9:50

March 2001		66:00		23:25		7:41

Sept. 2001		72:00		21:41		6:24

March 2002		70:00		31:18		8:51

Sept. 2002		72:00		16:31		13:58

March 2003		Note: No response. Field Report Group has opened an investigation.

Sample Number: 009

# Response Time in Minutes

Sensitivity		70 ppm CO 	150 ppm CO	400 ppm CO

## March 1999		(41) 205:48	(104) 49:54	(316) 13:12

July 1999		(35) No alarm	(86) 60:15	(235) 21:06

Oct. 1999		(0) No alarm	(65) No alarm	(204) 24:20

March 2000		(0) No alarm	(64) 116:00	(196) 25:20

Sept. 2000		(0) No alarm	(53) 140:00	(166) 35:18

March 2001		(0) No alarm	(51) 157:00	(160) 41:15

Sept. 2001		(0) No alarm	(0) No alarm	(118) 49:47

March 2002		(0) No alarm	(0) No alarm	(120) 48:57

Sept. 2002		(0) No alarm	(0) No alarm	(92) 75:00

March 2003		Note: Sample has been recalled in industry.

Sample Number: 029

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		82:33		10:51		11:30

July 1999		Note: Unit not yet distributed.  Unit is powered in lab.

Oct. 1999		88:00		12:05		11:02

March 2000		83:00		11:46		11:23

Sept. 2000		81:00		11:53		11:15

March 2001		75:00		11:22		11:01

Sept. 2001		72:00		11:31		10:20

March 2002		82:00		11:31		10:27

Sept. 2002		83:00		11:16		10:49

March 2003		88:00		10:57		9:45

Sept. 2004		81:00		11:10		10:59

March 2004		83:00		12:04		10:24

Sample Number: 030

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		85:18		10:55		11:56

July 1999		Note: Unit not yet distributed.  Unit is powered in lab.

Oct. 1999		86:00		12:47		11:35

March 2000		85:00		12:23		11:43

Sept. 2000		Note: Sample out of survey.

Sample Number: 031

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		85:29		11:10		11:53

July 1999		Note: Supervised failure in the field – trouble signal.

Sample Number: 032

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		25:32		5:33		4:41

July 1999		26:32		6:01		4:51

Oct. 1999		22:04		6:51		6:02

March 2000		14:45		7:14		6:07

Sept. 2000		Note: Sample has been removed from survey by UL Field Report Group.

Sample Number: 033

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		88:44		27:51		8:04

July 1999		38:15		13:14		4:33

Oct. 1999		89:00		33:22		11:49

March 2000		58:10		14:48		6:33

Sept. 2000		60:00		15:05		6:23

March 2001		61:00		33:40		6:18

Sept. 2001		Note: Sample out of survey.

Sample Number: 034

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		89:50		29:30		7:05

July 1999		120:43		58:27		12:24

Oct. 1999		120:00		58:21		13:05

March 2000		118:00		33:42		13:45

Sept. 2000		101:00		36:22		11:14

March 2001		98:00		39:22		9:03

Sept. 2001		90:00		41:02		10:24

March 2002		110:00		38:21		12:15

Sept. 2002		108:00		44:32		14:24

March 2003		242:00		89:00		19:24

Sept. 2004		225:00		79:00		26:40

March 2004		Note: Sample out of survey.

Sample Number: 035

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		70:23		18:36		7:31

July 1999		60:11		19:50		8:20

Oct. 1999		87:00		43:02		13:47

March 2000		62:00		34:51		8:38

Sept. 2000		61:00		25:51		6:40

March 2001		64:00		19:40		5:31

Sept. 2001		87:00		19:25		5:05

March 2002		110:00		38:21		12:15

Sept. 2002		68:00		22:24		4:50

March 2003		44:09		14:12		6:44

Sept. 2004		46:48		10:54		6:23

March 2004		62:00		10:31		9:58

Sample Number: 036

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		72:25		15:25		5:24

July 1999		60:25		32:41		8:58

Oct. 1999		64:00		35:31		8:26

March 2000		80:00		29:37		6:34

Sept. 2000		82:00		28:42		6:24

March 2001		65:00		21:15		5:37

Sept. 2001		62:00		13:46		5:38

March 2002		29:33		17:54		4:26

Sept. 2002		18:36		8:41		5:34

March 2003		25:38		7:20		5:19

Sept. 2004		26:04		7:10		5:45

March 2004		19:07		14:16		4:24

Sample Number: 037

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		108:37		29:41		5:47

July 1999		120:16		60:02		18:55

Oct. 1999		166:00		102:00		21:12

March 2000		98:00		59:42		9:22

Sept. 2000		96:00		37:45		6:29

March 2001		92:00		40:29		9:07

Sept. 2001		82:00		36:25		12:12

March 2002		86:00		20:42		7:14

Sept. 2002		103:00		21:58		7:01

March 2003		89:00		25:01		6:08

Sept. 2004		89:00		15:49		5:46

March 2004		65:00		16:25		5:16

Sample Number: 038

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		116:31		28:37		6:20

July 1999		180:01		59:16		13:47

Oct. 1999		115:00		47:15		14:12

March 2000		130:00		48:58		14:28

Sept. 2000		124:00		45:22		12:10

March 2001		125:00		46:37		10:32

Sept. 2001		126:00		44:23		5:50

March 2002		126:00		25:35		12:41

Sept. 2002		137:00		22:24		4:58

March 2003		97:00		29:31		7:17

Sept. 2004		110:00		19:15		6:32

March 2004		92:00		15:23		4:31

Sample Number: 039

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		119:44		29:13		8:55

July 1999		120:33		42:20		10:29

Oct. 1999		119:00		48:27		14:44

March 2000		113:00		35:51		9:33

Sept. 2000		118:00		30:23		8:01

March 2001		102:00		25:20		8:20

Sept. 2001		106:00		29:44		13:25

March 2002		90:00		27:54		7:30

Sept. 2002		88:00		30:48		8:26

March 2003		88:00		21:41		5:20

Sept. 2004		65:00		14:35		5:47

March 2004		77:00		15:41		5:31

Sample Number: 040

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		106:26		29:02		5:29

July 1999		60:09		29:10		8:37

Oct. 1999		89:00		31:25		7:43

March 2000		90:00		24:27		9:30

Sept. 2000		94:00		32:16		8:56

March 2001		95:00		32:27		9:10

Sept. 2001		93:00		35:16		11:23

March 2002		88:00		20:50		7:12

Sept. 2002		87:00		30:10		8:36

March 2003		89:00		19:13		5:26

Sept. 2004		67:00		13:39		5:45

March 2004		72:00		14:19		5:06

Sample Number: 058

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		99:00		22:30		7:32

July 1999		60:41		24:31		8:15

Oct. 1999		88:00		24:30		8:35

March 2000		99:00		23:35		7:21

Sept. 2000		102:00		24:41		10:16

March 2001		104:00		24:18		9:39

Sept. 2001		104:00		26:10		8:56

March 2002		100:00		23:38		9:53

Sept. 2002		99:00		22:47		7:41

March 2003		99:00		24:31		7:29

Sept. 2004		98:00		25:20		8:37

March 2004		68:00		12:37		6:42

Sample Number: 059

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		89:00		20:39		7:14

July 1999		Note: Unit not yet distributed.  Unit is powered in lab.

Oct. 1999		84:00		23:07		8:10

March 2000		100:00		23:39		7:24

Sept. 2000		123:00		32:07		8:20

March 2001		101:00		27:30		7:14

Sept. 2001		119:00		26:38		8:55

March 2002		100:00		25:31		7:50

Sept. 2002		98:00		24:36		7:30

March 2003		99:00		24:32		7:08

Sept. 2004		98:00		24:47		5:38

March 2004		Note: Sample out of survey.

Sample Number: 060

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		94:00		20:14		6:36

July 1999		Note: Unit not yet distributed.  Unit is powered in lab.

Oct. 1999		100:00		24:48		5:45

March 2000		99:00		22:47		7:32

Sept. 2000		99:00		22:23		6:44

March 2001		103:00		24:45		6:58

Sept. 2001		110:00		24:06		7:44

March 2002		99:00		22:30		6:14

Sept. 2002		140:00		48:39		14:20

March 2003		105:00		26:04		8:45

Sept. 2004		123:00		23:39		8:25

March 2004		Note: Supervised failure in the field - power on LED de-energized.

Sample Number: 061

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		98:40		26:30		5:27

July 1999		35:36		10:26		6:31

Oct. 1999		115:00		46:43		23:16

March 2000		101:00		28:25		9:36

Sept. 2000		104:00		25:31		8:11

March 2001		98:00		23:31		9:25

Sept. 2001		101:00		23:41		6:10

March 2002		101:00		12:52		6:30

Sept. 2002		125:00		24:10		8:34

March 2003		128:00		23:29		10:03

Sept. 2004		131:00		24:12		6:43

March 2004		120:00		25:53		6:22

Sample Number: 062

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		90:15		23:14		5:38

July 1999		24:44		13:44		6:36

Oct. 1999		150:00		60:16		9:35

March 2000		63:00		21:45		9:03

Sept. 2000		82:00		28:07		6:10

March 2001		73:00		27:37		7:49

Sept. 2001		54:00		23:14		7:22

March 2002		85:00		22:25		7:46

Sept. 2002		103:00		22:49		6:33

March 2003		Note: Sample out of survey.

Sample Number: 063

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		99:10		23:42		8:06

July 1999		61:31		15:51		9:10

Oct. 1999		123:00		60:40		10:27

March 2000		99:00		28:23		9:35

Sept. 2000		90:00		24:50		7:23

March 2001		100:00		21:20		8:14

Sept. 2001		Note: Supervised failure in the field – power on LED de-energized.

Sample Number: 064

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		25:40		19:57		7:45

July 1999		60:43		29:43		8:18

Oct. 1999		99:00		30:04		8:41

March 2000		105:00		27:48		9:51

Sept. 2000		115:00		24:30		5:14

March 2001		109:00		31:15		7:55

Sept. 2001		102:00		38:28		14:50

March 2002		112:00		41:35		8:05

Sept. 2002		110:00		48:20		14:40

March 2003		113:00		39:52		9:58

Sept. 2004		110:00		37:51		8:40

March 2004		Note: Sample out of survey.

Sample Number: 065

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		24:49		19:42		4:57

## July 1999		25:23		9:35		6:41

Oct. 1999		96:00		23:45		8:39

March 2000		94:00		22:24		4:42

Sept. 2000		97:00		21:31		5:04

March 2001		89:00		24:15		7:11

Sept. 2001		Note: No data for sample.

March 2002		105:00		35:14		7:18

Sept. 2002		106:00		34:22		8:51

March 2003		76:00		23:44		8:13

Sept. 2004		121:00		27:41		8:43

March 2004		Note: Sample out of survey.

Sample Number: 066

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		23:20		17:26		7:15

July 1999		60:48		10:31		7:50

Oct. 1999		100:00		24:50		5:47

March 2000		104:00		23:11		7:04

Sept. 2000		Note: Sample out of survey.

Sample Number: 130

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		101:00		11:02		6:40

July 1999		60:28		11:06		7:02

Oct. 1999		101:00		24:42		5:51

March 2000		101:00		32:27		7:21

Sept. 2000		103:00		29:41		7:37

March 2001		107:00		22:41		6:49

Sept. 2001		109:00		30:45		8:03

March 2002		100:00		25:24		7:30

Sept. 2002		100:00		25:22		7:20

March 2003		101:00		24:32		7:01

Sept. 2004		103:00		15:25		5:25

March 2004		120:00		23:40		6:10

Sample Number: 131

# Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		100:00		11:15		7:31

July 1999		25:54		10:25		6:56

Oct. 1999		100:00		24:12		8:35

March 2000		101:00		24:25		9:36

Sept. 2000		104:00		24:23		5:06

March 2001		100:00		26:25		9:32

Sept. 2001		91:00		26:51		10:39

March 2002		102:00		25:36		9:41

Sept. 2002		103:00		30:20		12:30

March 2003		101:00		31:27		9:14

Sept. 2004		101:00		36:24		10:20

March 2004		113:00		34:11		11:15

## Sample Number: 132

## Response Time in Minutes

Sensitivity		70 ppm CO	150 ppm CO	400 ppm CO

## March 1999		97:00		12:29		7:06

July 1999		32:41		11:40		7:58

Oct. 1999		101:00		24:15		9:25

March 2000		101:00		24:22		9:12

Sept. 2000		100:00		25:05		6:38

March 2001		106:00		36:52		8:32

Sept. 2001		Note: No data for sample.

March 2002		79:00		39:38		9:32

Sept. 2002		Note: No data for sample.

March 2003		250:00		101:00		24:33

Sept. 2003		Note: Sample out of survey.

(Display Raeding)